## NR
| TABLE-1 |  |  |  | Annexure-IV
Region wise information ( Average for the year, but otherwise total for the Region ) for AC System
| Name of Transmission company : | POWERGRID CORPORATION OF INDIA LTD
| Name of Region | NORTHERN REGION
Sl No | Details of Information | 2002-03 | 2003-04 | 2004-05 | 2005-06 | 2006-07
1 | Average number of AC Sub-Station in Operation | 15.5 | 17 | 17 | 18.5 | 22
2 | Average Ckt Kms of AC lines in Operation | 13598.09 | 14529.45 | 14699.01 | 15910.27 | 18154.7
3 | Total number of Employees engaged in Sub-Station O&M | 809 | 745 | 768 | 755 | 818
4 | Total number of Employees engaged in Line O&M | 477 | 432 | 319 | 298 | 346
5 | Auxillary power consumption in MU ( excluding colony power) | 10.18 | 10.48 | 10.3 | 10.94 | 13.05
6 | Colony Power consumption (MU) | 3.51 | 3.35 | 3.55 | 3.65 | 3.93
7 | Average outage duration ( Hours/year ) for
7.1 | Transmission Line
| (i) On POWERGRID's account | 23.825 | 31.26 | 20.453 | 18.44 | 28.947
| (ii) Outages as per Clause 6(i)&(ii) of CERC Regulations dt 26.03.2004 - Others | 101.888 | 80.941 | 113.494 | 25.608 | 23.515
| (iii) Outage as per Clause 5(i)&(ii) of CERC Regulations dt 26.03.2004 - Deemed available | 204.431 | 369.066 | 360.047 | 175.361 | 204.034
7.2 | Transformers
| (i) On POWERGRID's account | 87.171 | 114.882 | 29.365 | 15.694 | 373.665
| (ii) Outages as per Clause 6(i)&(ii) of CERC Regulations dt 26.03.2004 - Others | 60.913 | 2.039 | 14.868 | 14.41 | 3.533
| (iii) Outage as per Clause 5(i)&(ii) of CERC Regulations dt 26.03.2004 - Deemed available | 201.73 | 241.817 | 240.089 | 33.442 | 19.445
7.3 | Bus Reactors
| (i) On POWERGRID's account | 4.365 | 158.286 | 4.721 | 3.064 | 3.559
| (ii) Outages as per Clause 6(i)&(ii) of CERC Regulations dt 26.03.2004 - Others | 0 | 0 | 0 | 0 | 0.091
| (iii) Outage as per Clause 5(i)&(ii) of CERC Regulations dt 26.03.2004 - Deemed available | 2465.771 | 2533.418 | 3549.141 | 3989.761 | 3382.33
8 | Cost of spares ( Rs in Lakhs)
| a) Capitalized | 2298.26 | 2502 | 2502 | 2988.88 | 4326.1
| b) Consumed | Data separately not available / maintained
| c) In Stock | Data separately not available / maintained
TABLE-2
Station wise information ( Average for the year, but otherwise total for the Station) for HVDC System
| Name of the HVDC Station | Rihand -Dadri HVDC System
Sl No | Details of Information | 2002-03 | 2003-04 | 2004-05 | 2005-06 | 2006-07
1 | Total number of Employees engaged in Sub-Station O&M - At Rihand | 42 | 32 | 27 | 26 | 26
2 | Total number of Employees engaged in Sub-Station O&M - At Dadri | 45 | 32 | 35 | 35 | 33
3 | Total number of Employees engaged in Line O&M | 31 | 24 | 35 | 22 | 19
4 | Auxillary power consumption in MU ( excluding colony power) - at Rihand | 4.92 | 4.75 | 5.2 | 4.16 | 4.56
TABLE-2
Station wise information ( Average for the year, but otherwise total for the Station) for HVDC System | [5 empty] | Annexure-IV
| Name of Transmission company : | POWERGRID CORPORATION OF INDIA LTD
| Name of Region | NORTHERN REGION
| Name of the HVDC Station | Rihand -Dadri HVDC System
5 | Auxillary power consumption in MU ( excluding colony power) - at Dadri | 4.5 | 5 | 5.16 | 5.31 | 4.44
6 | Colony Power consumption (MU) | No POWERGRID colony at Rihand
No POWERGRID colony at Dadri
7 | Outage duration in Pole-days
| (i) On POWERGRID's account* | 46.19 | 23.18 | 7.26 | 22.34 | 80.24
| (ii) Outages as per Clause 6(i)&(ii) of CERC Regulations dt 26.03.2004 - Others | 0.02 | 0 | 0 | 0 | 0
| (iii) Outage as per Clause 5(i)&(ii) of CERC Regulations dt 26.03.2004 - Deemed available | 0 | 0 | 0.52 | 0.16 | 0.29
8 | Loading curtailment in MW -days | Data is under compilation and shall be furnished subsequently
9 | Cost of spares ( Rs in Lakhs)
| a) Capitalized ( For Rihand Stg-I Tr System) - Combined for Rihand & DADRI HVDC & AC Portion | 5611 | 5611 | 5611 | 5611 | 5611
| b) Consumed | Data separately not available / maintained
| c) In Stock | Data separately not available / maintained
* As per availability certificate issued by RPC
| Name of the HVDC Station | Vindhyachal HVDC
Sl No | Details of Information | 2002-03 | 2003-04 | 2004-05 | 2005-06 | 2006-07
1 | Total number of Employees engaged in Sub-Station O&M | 26 | 27 | 24 | 23 | 25
2 | Total number of Employees engaged in Line O&M | 0 | 0 | 0 | 0 | 0
3 | Auxillary power consumption in MU ( excluding colony power) | 3.92 | 3.67 | 3.81 | 3.78 | 3.35
4 | Colony Power consumption (MU) | No POWERGRID colony at Vindhyachal
5 | Outage duration in Pole-days
| (i) On POWERGRID's account* | 8.42 | 2.11 | 5.11 | 5.55 | 5.15
| (ii) Outages as per Clause 6(i)&(ii) of CERC Regulations dt 26.03.2004 - Others | 0.77 | 0.28 | 1.07 | 0.06 | 0.13
| (iii) Outage as per Clause 5(i)&(ii) of CERC Regulations dt 26.03.2004 - Deemed available | 1.25 | 1.78 | 0.39 | 0.85 | 0.18
6 | Loading curtailment in MW -days | Data is under compilation and shall be furnished subsequently
7 | Cost of spares ( Rs in Lakhs)
| a) Capitalized | 4.47 | 4.47 | 4.47 | 4.47 | 4.47
| b) Consumed | Data separately not available / maintained
| c) In Stock | Data separately not available / maintained
* As per availability certificate issued by RPC

## SR
| TABLE-1 |  |  |  |  | Annexure-IV
Region wise information ( Average for the year, but otherwise total for the Region ) for AC System
| Name of Transmission company : | POWERGRID CORPORATION OF INDIA LTD
| Name of Region | SOUTHERN REGION
Sl No | Details of Information | 2002-03 | 2003-04 | 2004-05 | 2005-06 | 2006-07
1 | Average number of AC Sub-Station in Operation | 17.5 | 19.5 | 20 | 21 | 22.5
2 | Average Ckt Kms of AC lines in Operation | 7686.402 | 8731.433 | 9545.001 | 10668.773 | 11378.262
3 | Total number of Employees engaged in Sub-Station O&M | 415.38 | 447.08 | 430.86 | 450.4 | 443.16
4 | Total number of Employees engaged in Line O&M | 146.62 | 159.92 | 170.14 | 181.4 | 175.66
5 | Auxillary power consumption in MU ( excluding colony power) | 10.3377 | 12.513 | 12.8959 | 8.8695 | 10.0164
Seprate meters for colony power not available for all S/Stn in the Region during the period and the colony power consumption is included in station consumption
6 | Colony Power consumption (MU) |  |  |  | 3.131 | 3.24
7 | Average outage duration ( Hours/year ) for
7.1 | Transmission Line
| (i) On POWERGRID's account | 18.71 | 14.67 | 15.81 | 9.56 | 12.22
| (ii) Outages as per Clause 6(i)&(ii) of CERC Regulations dt 26.03.2004 - Others | 15.12 | 28.53 | 12.02 | 9.77 | 4.96
| (iii) Outage as per Clause 5(i)&(ii) of CERC Regulations dt 26.03.2004 - Deemed available | 93.19 | 275.6 | 223.06 | 544.14 | 298.36
7.2 | Transformers
| (i) On POWERGRID's account | 11.64 | 118.13 | 18.44 | 77.54 | 40.26
| (ii) Outages as per Clause 6(i)&(ii) of CERC Regulations dt 26.03.2004 - Others | 5.475 | 2.25 | 1.54 | 3.48 | 2.81
| (iii) Outage as per Clause 5(i)&(ii) of CERC Regulations dt 26.03.2004 - Deemed available | 40.56 | 6.47 | 15.08 | 4.18 | 7.45
7.3 | c) Bus Reactors
| (i) On POWERGRID's account | 8.96 | 8.53 | 4.53 | 34.03 | 5.33
| (ii) Outages as per Clause 6(i)&(ii) of CERC Regulations dt 26.03.2004 - Others | 0 | 0.11 | 0 | 0 | 0
| (iii) Outage as per Clause 5(i)&(ii) of CERC Regulations dt 26.03.2004 - Deemed available | 3570.45 | 1443.76 | 1089.09 | 738.5 | 1418.23
8 | Cost of spares ( Rs in Lakhs)
| a) Capitalized | 2787.48 | 2925.05 | 3227.41 | 3652.47 | 3942.05
| b) Consumed | Data separately not available / maintained
| c) In Stock | Data separately not available / maintained
| TABLE-2 |  |  |  |  | Annexure-IV
Station wise information ( Average for the year, but otherwise total for the Station) for HVDC System
| Name of Transmission company : | POWERGRID CORPORATION OF INDIA LTD
| Name of HVDC Station | GAJUWAKA HVDC
Sl No | Details of Information | 2002-03 | 2003-04 | 2004-05 | 2005-06 | 2006-07
1 | Total number of Employees engaged in Sub-Station O&M | 55 | 58 | 48 | 35 | 40
2 | Total number of Employees engaged in Line O&M | 0 | 0 | 0 | 0 | 0
3 | Auxillary power consumption in MU ( excluding colony power) | 2.3453 | 2.9261 | 4.2929 | 6.054 | 6.5494
|  | For Pole-I only |  | Pole-II DOCO 01.03.2005
4 | Colony Power consumption (MU) | Meters not installed |  | 0.5319 | 0.51538 | 0.50205
5 | Outage duration in Pole-days
| (i) On POWERGRID's account** | 36.2758 | 113.06 | 1.35 | 12.99 | 10.99
| (ii) Outages as per Clause 6(i)&(ii) of CERC Regulations dt 26.03.2004 - Others | 0.028125 | 0.15 | 0.025625 | 0 | 0.05875
| (iii) Outage as per Clause 5(i)&(ii) of CERC Regulations dt 26.03.2004 - Deemed available | 0 | 0 | 0.24313 | 0 | 0
** As per availability certificate issued by RPC
6 | Loading curtailment in MW -days | Data is under compilation and shall be furnished subsequently
7 | Cost of spares ( Rs in Lakhs)
| a) Capitalized | 439.18 | 439.18 | 1002.02 | 1002.02 | 1002.02
| b) Consumed | Data separately not available / maintained
| c) In Stock | Data separately not available / maintained
| Name of HVDC Station | TALCHER - KOLAR HVDC SYSTEM
Sl No | Details of Information | 2002-03 | 2003-04 | 2004-05 | 2005-06 | 2006-07
1 | Total number of Employees engaged in Sub-Station O&M - At Talcher HVDC | 40 | 39 | 34 | 31 | 25
2 | Total number of Employees engaged in Sub-Station O&M - At Kolar HVDC | 34 | 34 | 34 | 33 | 34
3 | Total number of Employees engaged in Line O&M | 33 | 38 | 37 | 36 | 37
4 | Auxillary power consumption in MU ( excluding colony power) - At Talcher | Commisioned during the year | 4.5705 | 4.771 | 5.4528 | 5.3806
5 | Auxillary power consumption in MU ( excluding colony power) - At Kolar | Commisioned during the year | 6.7746 | 5.8194 | 5.23 | 5.202
6 | Colony Power consumption (MU) - At Talcher | No POWERGRID colony at Talcher
| Colony Power consumption (MU) - At Kolar | 0.074 | 0.208 | 0.297 | 0.923 | 0.889
7 | Outage duration in Pole-days
| (i) On POWERGRID's account** | 9.5077 | 21.76 | 13.98 | 7.99 | 11.02
| (ii) Outages as per Clause 6(i)&(ii) of CERC Regulations dt 26.03.2004 - Others | 0 | 0.35146 | 0 | 0.26771 | 0.09125
| (iii) Outage as per Clause 5(i)&(ii) of CERC Regulations dt 26.03.2004 - Deemed available | 0.19625 | 0.59479 | 2.0004 | 0 | 0
** As per availability certificate issued by RPC
6 | Loading curtailment in MW -days | Data is under compilation and shall be furnished subsequently
7 | Cost of spares ( Rs in Lakhs)
| a) Capitalized ( For Talcher-Kolar Pole-I & II & AC lines combined) | 9793.07 | 9793.07 | 9793.07 | 9793.07 | 9793.07
| b) Consumed | Data separately not available / maintained
| c) In Stock | Data separately not available / maintained

## ER
| TABLE-1 |  |  |  |  | Annexure-IV
Region wise information ( Average for the year, but otherwise total for the Region ) for AC System
| Name of Transmission company : | POWERGRID CORPORATION OF INDIA LTD
| Name of Region | EASTERN REGION
Sl No | Details of Information | 2002-03 | 2003-04 | 2004-05 | 2005-06 | 2006-07
1 | Average number of AC Sub-Station in Operation | 14.5 | 16 | 17.5 | 19 | 21
2 | Average Ckt Kms of AC lines in Operation | 5508.4 | 5839.4 | 6563.06 | 7343.008 | 7891.479
3 | Total number of Employees engaged in Sub-Station O&M | 541 | 546 | 553 | 576 | 642.5
4 | Total number of Employees engaged in Line O&M | 164 | 158 | 146 | 116 | 177.5
5 | Auxillary power consumption in MU ( excluding colony power) | 5.8378 | 5.6972 | 6.866 | 7.9023 | 9.6462
6 | Colony Power consumption (MU) | 3.0459 | 2.7512 | 3.1868 | 3.239 | 3.1954
7 | Average outage duration ( Hours/year ) for
7.1 | Transmission Line
| (i) On POWERGRID's account | 36 | 24.4 | 15.14 | 16.86 | 24.88
| (ii) Outages as per Clause 6(i)&(ii) of CERC Regulations dt 26.03.2004 - Others | 405 | 52.06 | 27.05 | 14.14 | 28.09
| (iii) Outage as per Clause 5(i)&(ii) of CERC Regulations dt 26.03.2004 - Deemed available | 182.68 | 384.83 | 277.54 | 259.09 | 302.74
7.2 | Transformers
| (i) On POWERGRID's account | 43 | 13.5 | 4.9 | 82.16 | 120.36
| (ii) Outages as per Clause 6(i)&(ii) of CERC Regulations dt 26.03.2004 - Others | 6.14 | 8.07 | 9.5 | 6.86 | 18.47
| (iii) Outage as per Clause 5(i)&(ii) of CERC Regulations dt 26.03.2004 - Deemed available | 4.02 | 1.23 | 2.12 | 4.55 | 2.81
7.3 | c) Bus Reactors
| (i) On POWERGRID's account | 59 | 2.1 | 0 | 0 | 0.68
| (ii) Outages as per Clause 6(i)&(ii) of CERC Regulations dt 26.03.2004 - Others | 498.28 | 0 | 0.19 | 0 | 0
| (iii) Outage as per Clause 5(i)&(ii) of CERC Regulations dt 26.03.2004 - Deemed available | 289.67 | 239.12 | 424.51 | 186.7 | 385.04
8 | Cost of spares ( Rs in Lakhs)
| a) Capitalized | 494.47 | 674.87 | 969.58 | 2137.38 | 2805.06
| b) Consumed | Data separately not available / maintained
| c) In Stock | Data separately not available / maintained
| TABLE-2 |  |  |  | Annexure-IV
Station wise information ( Average for the year, but otherwise total for the Station) for HVDC System
| Name of Transmission company : | POWERGRID CORPORATION OF INDIA LTD
| Name of Region | EASTERN REGION
| Nmae of the HVDC Station | SASARAM
Sl No | Details of Information | 2002-03 | 2003-04 | 2004-05 | 2005-06 | 2006-07
1 | Total number of Employees engaged in Sub-Station O&M | 34 | 30 | 26 | 26 | 24
2 | Total number of Employees engaged in Line O&M | 0 | 0 | 0 | 0 | 0
3 | Auxillary power consumption in MU ( excluding colony power) | 1.7646** | 4.9438 | 4.4301 | 5.1935 | 5.2062
4 | Colony Power consumption (MU) | 0.0879** | 0.3303 | 0.2771 | 0.2602 | 0.2383
5 | Outage duration in Pole-days
| (i) On POWERGRID's account* | 1.77 | 14.79 | 34 | 8.4167 | 3.25
| (ii) Outages as per Clause 6(i)&(ii) of CERC Regulations dt 26.03.2004 - Others | 0.19 | 0.95 | 0.91 | 0 | 0
| (iii) Outage as per Clause 5(i)&(ii) of CERC Regulations dt 26.03.2004 - Deemed available | 0 | 0 | 0.52 | 0 | 1.46
* As per availability certificate issued by RPC
6 | Loading curtailment in MW -days | Data is under compilation and shall be furnished subsequently
7 | Cost of spares ( Rs in Lakhs)
| a) Capitalized ( Sasaram HVDC & AC lines) | 827.72 | 827.72 | 827.72 | 827.72 | 827.72
| b) Consumed | Data separately not available / maintained
| c) In Stock | Data separately not available / maintained
** DOCO of the pole is 01.12.02

## WR
| TABLE-1 |  |  |  |  | Annexure-IV
Region wise information ( Average for the year, but otherwise total for the Region ) for AC System
| Name of Transmission company : | POWERGRID CORPORATION OF INDIA LTD
| Name of Region | WESTERN REGION
Sl No | Details of Information | 2002-03 | 2003-04 | 2004-05 | 2005-06 | 2006-07
1 | Average number of AC Sub-Station in Operation | 6.5 | 7 | 7.5 | 9 | 10
2 | Average Ckt Kms of AC lines in Operation | 9342 | 10316.65 | 10419.49 | 10976.52 | 11716.355
3 | Total number of Employees engaged in Sub-Station O&M | 199 | 199 | 281 | 281 | 334
4 | Total number of Employees engaged in Line O&M | 160 | 160 | 162 | 174 | 187
5 | Auxillary power consumption in MU ( excluding colony power) | 7.63 | 7.35 | 8.52 | 9.77 | 9.82
6 | Colony Power consumption (MU) | 1.05 | 0.92 | 1.16 | 1.21 | 1.34
7 | Average outage duration ( Hours/year ) for
7.1 | Transmission Line
| (i) On POWERGRID's account | 29.831 | 17.65 | 23.93 | 25.56 | 23.25
| (ii) Outages as per Clause 6(i)&(ii) of CERC Regulations dt 26.03.2004 - Others | 14.55 | 84.96 | 17.37 | 28.13 | 20.12
| (iii) Outage as per Clause 5(i)&(ii) of CERC Regulations dt 26.03.2004 - Deemed available | 141.13 | 285.66 | 163.83 | 297.58 | 194.42
7.2 | Transformers
| (i) On POWERGRID's account | 24.38 | 46.58 | 10.82 | 27.47 | 19.93
| (ii) Outages as per Clause 6(i)&(ii) of CERC Regulations dt 26.03.2004 - Others | 0.04 | 5.79 | 0.32 | 1.92 | 0.88
| (iii) Outage as per Clause 5(i)&(ii) of CERC Regulations dt 26.03.2004 - Deemed available | 25.99 | 58.08 | 47.22 | 10.1 | 70.72
7.3 | c) Bus Reactors
| (i) On POWERGRID's account | 0 | 0.91 | 1 | 0 | 0
| (ii) Outages as per Clause 6(i)&(ii) of CERC Regulations dt 26.03.2004 - Others | 0 | 0 | 0 | 0 | 0
| (iii) Outage as per Clause 5(i)&(ii) of CERC Regulations dt 26.03.2004 - Deemed available | Bus reactors were taken out of service as per instruction of RLDC for voltage regulation
8 | Cost of spares ( Rs in Lakhs)
| a) Capitalized | 443.2 | 962.15 | 1108.49 | 2530.62 | 2717.14
| b) Consumed | Data separately not available / maintained
| c) In Stock | Data separately not available / maintained
TABLE-2
Station wise information ( Average for the year, but otherwise total for the Station) for HVDC System
| Name of Transmission company : | POWERGRID CORPORATION OF INDIA LTD
| Name of Region | WESTERN REGION |  |  | Annexure-IV
| Name of HVDC Station | BHADRAWATI
Sl No | Details of Information | 2002-03 | 2003-04 | 2004-05 | 2005-06 | 2006-07
1 | Total number of Employees engaged in Sub-Station O&M | 31 | 31 | 31 | 31 | 31
2 | Total number of Employees engaged in Line O&M | 0 | 0 | 0 | 0 | 0
3 | Auxillary power consumption in MU ( excluding colony power) | 4.04 | 4.173 | 4.172 | 5.395 | 4.76
4 | Colony Power consumption (MU) | Colony common for both HVDC and AC S/stns. Colony power consumption shown in AC system of the Region.
5 | Outage duration in Pole-days
| (i) On POWERGRID's account* | 13.092 | 29.705 | 23.87 | 3.1569 | 9.89
| (ii) Outages as per Clause 6(i)&(ii) of CERC Regulations dt 26.03.2004 - Others | 0 | 0.063 | 0.024 | 0 | 0.01
| (iii) Outage as per Clause 5(i)&(ii) of CERC Regulations dt 26.03.2004 - Deemed available | 0 | 0.495 | 0.083 | 0 | 0
6 | Loading curtailment in MW -days | Data is under compilation and shall be furnished subsequently
7 | Cost of spares ( Rs in Lakhs )
| a) Capitalized | 2013.04 | 2013.04 | 2013.04 | 2013.04 | 2013.04
| b) Consumed | Data separately not available / maintained
| c) In Stock | Data separately not available / maintained
* As per availability certificate issued by RPC

## NER
| TABLE-1 |  |  |  |  | Annexure-IV
Region wise information ( Average for the year, but otherwise total for the Region ) for AC System
| Name of Transmission company : | POWERGRID CORPORATION OF INDIA LTD
| Name of Region | NORTH EASTERN REGION
Sl No | Details of Information | 2002-03 | 2003-04 | 2004-05 | 2005-06 | 2006-07
1 | Average number of AC Sub-Station in Operation | 12 | 12 | 13 | 13 | 13
2 | Average Ckt Kms of AC lines in Operation | 4949.67 | 4949.67 | 4994.21 | 4994.21 | 4994.21
3 | Total number of Employees engaged in Sub-Station O&M | 595.04 | 558.84 | 551.1 | 514.8 | 495.6
4 | Total number of Employees engaged in Line O&M | 184.96 | 174.16 | 157.9 | 161.2 | 158.4
5 | Auxillary power consumption in MU ( excluding colony power) | 2.3353 | 2.3641 | 3.6341 | 4.1212 | 3.2679
6 | Colony Power consumption (MU) | 1.565 | 1.1938 | 1.3073 | 1.2762 | 1.7312
7 | Average outage duration ( Hours/year ) for
7.1 | Transmission Line
| a) On POWERGRIDs account | 84.87 | 78.11 | 63.49 | 77.63 | 79.75
| (ii) Outages as per Clause 6(i)&(ii) of CERC Regulations dt 26.03.2004 - Others | 274.66 | 151.34 | 332.72 | 179.77 | 70.02
| (iii) Outage as per Clause 5(i)&(ii) of CERC Regulations dt 26.03.2004 - Deemed available | 449.03 | 287.97 | 379.48 | 344.6 | 460.51
7.2 | Transformers
| a) On POWERGRIDs account | 92.45 | 19.94 | 23.18 | 281.85 | 86.88
| (ii) Outages as per Clause 6(i)&(ii) of CERC Regulations dt 26.03.2004 - Others | 0.97 | 0.65 | 0.25 | 0.12 | 0
| (iii) Outage as per Clause 5(i)&(ii) of CERC Regulations dt 26.03.2004 - Deemed available | 0.79 | 0 | 0.12 | 0 | 0
7.3 | Bus Reactors
| a) On POWERGRIDs account | 22.94 | 19.99 | 29.52 | 4.97 | 0.3
| (ii) Outages as per Clause 6(i)&(ii) of CERC Regulations dt 26.03.2004 - Others | 0 | 0.07 | 0 | 0 | 0
| (iii) Outage as per Clause 5(i)&(ii) of CERC Regulations dt 26.03.2004 - Deemed available | 1064.93 | 2761.88 | 2776.01 | 2857.72 | 2619.29
8 | Cost of spares ( Rs in Lakhs)
| a) Capitalized | Cost of spares capitalised not shown/maintained separately
| b) Consumed | Data separately not available / maintained
| c) In Stock | Data separately not available / maintained
| TABLE-2 |  |  |  | Annexure-IV
| Name of Transmission company : | POWERGRID CORPORATION OF INDIA LTD
| Name of Region | NORTH EASTERN REGION
Station wise information ( Average for the year, but otherwise total for the Station) for HVDC System
Sl No | Details of Information | 2002-03 | 2003-04 | 2004-05 | 2005-06 | 2006-07
1 | Total number of Employees engaged in Sub-Station O&M
2 | Total number of Employees engaged in Line O&M
3 | Auxillary power consumption in MU ( excluding colony power)
NOT APLLICABLE
4 | Colony Power consumption (MU)
5 | Outage duration in Pole-days
6 | Loading curtailment in MW -days
7 | Cost of spares (Rs in Lakhs)
a) Capitalized
b) Consumed
c) In Stock

## Notes
NOTES:
Annexure-IV
(1) | Average Number of AC S/Stns, Lines and manpower deployed is average of opening and closing figures during the year.
(2) | Average-Outage duration ( hrs/year) :-
(ii) Others account - As per clause 6 (i) & (ii) of Appendix III of CERC Regulation dt 29.03.2004
(III) Deemed avialable account - As per clause 5 (i) & (ii) of Appendix III of CERC Regulation dt 29.03.2004
(3) | Colony Power consumption (MU) has been indicated after installation of Energy meters for Colony seprately.
(4) | The details of cost of capitalised spares with respect to consumed and In-stock are not avialable / being maintained seprately and hence could not be furnished
(5) | Load curtailment in MW-days in respect of HVDC stations is under compilation and shall be furnished seprately.