## L
CERC
Capital Cost Benchmarking
Formatting of Headers / Dividers
| Sheet Header 1 | CERC | SheetHeader1
| Sheet Header 2 | Capital Cost Benchmarking | SheetHeader2
| Sheet Header 3 |  | SheetHeader3
| Header 1 | Header 1 | Header1
| Header 2 | Header 2 | Header2
| Header 3 | Header 3 | Header3
| Inputs Divider | Operational Assumptions | Inputs_Divider
| Table Heading 2 | Table Heading 2 | Table_Heading2
| Table Heading 3 | Table Heading 3
| Table Heading 4 | Table Heading 4
Individual Cell Assumptions
| Standard Assumption | 100 | Assumptions
| Offsheet Reference | 100 | Offsheet
| Flex Cell | 100 | Assumption_Flex
| Name Inputs | Cost Type | Technical_Input
| Technical Input | 1000 | Input
| Empy Cell |  | Empty_Cell
| Background for Flag | 0 | Flag
Infrastructure
| Sub-Total | Sub-Total | Sub-Total
| Line Total | 100 | Line_Summary
| Units | USD | Unit
| Operation Line (Non-Addition) | 100 | Line_Operation
| Operation (Addition / Total) | 100 | Line_Total
| Closing Balance | 100 | Line_ClosingBal
| Key Line | 100 | Line_Key
Development Styles
| WIP | W | WIP

## Cover
Central Electricity Regulatory Commission
Capital Cost Benchmarking for Transmission Sub-Station 400/220 kV

## User Guide
CERC
Capital Cost Benchmarking
| S.No. | Description
| 1 | The model for Transmission sub-station is meant to provide benchmark cost for selected configuration in terms of number of ICTs, reactors, bays etc.
| 2 | There are 20 standard configurations (called alternates here) provided in the model. The cost has been computed for each of the alternates.For example alternate-1 has configuration given below:-
|  | Number of Line Bays | 400 kV | 4
|  |  | 220 kV | 6
|  | Number of ICT Bays | 400 kV | 2
|  |  | 220 kV | 2
|  | Number of ICTs -Capacity in MVA | 315 | 2
|  |  | 500 | 0
|  | Number of Reactors | Shunt Reactor | 0
|  |  | Bus Reactor | 0
| 3 | The user has to select the alternate that matches the configuration as given by petitioner using drop down list given in cell C10 of Computation_sheet
| 4 | In case none of the alternates matches the configuration given by petitioner, user has to select the closest alternate that matches the configuration. The user may then add/substract components as given in cells C46 to C51 of "Computation_Sheet" to match the required configuration.
| 5 | The benchmark cost shall get computed in the cell C54 of "Computation_Sheet"
| 6 | The month and the year of escalation can be chosen from drop down list provided in cell D5
| 7 | The model can be updated by entering the value of indices in sheet named "Indices" for corresponding month and year. The user to refer to IEEMA publications for the same.

## Computation_Sheet
CERC
Capital Cost Benchmarking
 | time axis 2006-01-01 to 2014-03-01
| Choose Month and Year of Escalation |  | 2009-12-01
Choose Desired Configuration (from Alternates shown below)
| Choose Sub-Station Configuration | Alt - 11
| Descripction |  | Alt - 1 | Alt - 2 | Alt - 3 | Alt - 4 | Alt - 5 | Alt - 6 | Alt - 7 | Alt - 8 | Alt - 9 | Alt - 10 | Alt - 11 | Alt - 12 | Alt - 13 | Alt - 14 | Alt - 15 | Alt - 16 | Alt - 17 | Alt - 18 | Alt - 19 | Alt - 20
| Number of Line Bays | 400 kV | 4 | 4 | 4 | 4 | 2 | 2 | 6 | 4 | 11 | 6 | 2 | 2 | 2 | 6 | 4 | 2 | 2 | 12 | 7 | 4
|  | 220 kV | 6 | 6 | 6 | 4 | 4 | 4 | 6 | 11 | 12 | 6 | 4 | 4 | 4 | 6 | 6 | 4 | 4 | 5 | 0 | 0
| Number of ICT Bays | 400 kV | 2 | 2 | 2 | 2 | 2 | 1 | 2 | 1 | 2 | 2 | 2 | 2 | 1 | 2 | 3 | 2 | 2 | 2 | 0 | 0
|  | 220 kV | 2 | 2 | 2 | 2 | 2 | 1 | 2 | 1 | 2 | 2 | 2 | 2 | 1 | 2 | 3 | 2 | 2 | 2 | 0 | 0
| Number of ICTs -Capacity in MVA | 315 | 2 | 2 | 2 | 2 | 2 | 1 | 2 | 0 | 0 | 2 | 2 | 2 | 1 | 0 | 3 | 2 | 2 | 2 | 0 | 0
|  | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0
| Number of Reactors | Shunt Reactor | 0 | 2 | 4 | 2 | 2 | 2 | 2 | 3 | 5 | 2 | 1 | 0 | 1 | 2 | 2 | 0 | 2 | 4 | 2 | 2
|  | Bus Reactor | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 1 | 1 | 2 | 1 | 0 | 1 | 2 | 1 | 1
| Description | Alt - 11 | bar: Alt - 1
| Number of Line Bays | 400 kV | Alt - 1: 2
|  | 220 kV | Alt - 1: 4
| Number of ICT Bays | 400 kV | Alt - 1: 2
|  | 220 kV | Alt - 1: 2
| Number of ICTs -Capacity in MVA | 315 | Alt - 1: 2
|  | 500 | Alt - 1: 0
| Number of Reactors | Shunt Reactor | bar: Alt - 1
|  | Bus Reactor | Alt - 1: 0
For Modification in above configuration please choose from drop down list
| Combination Name | Configuration
| Combination-1 | 400 kV Line Bay with Shunt Reactor
| Combination-2 | 400kV Line Bay
| Combination-3 | 220KV Line Bay
| Combination-4 | 1 x 315 MVA ICT with 400 kV & 220 kV Bays
| Combination-5 | Addition of Shunt Reactor to 400KV Line Bay
| Combination-6 | 400 kV Bus Reactor Bay
|  | Component | Alt - 1: Add/ Subtract?; Alt - 18: 1
| Choose Combination to be added/ subtracted | None | Alt - 1: Add; Alt - 18: 1
| Choose Combination to be added/ subtracted | None | Alt - 1: Add; Alt - 18: 1
| Choose Combination to be added/ subtracted | None | Alt - 1: Add; Alt - 18: 1; Alt - 20: None | Alt - 1 | Alt - 2 | Alt - 3 | Alt - 4 | Alt - 5 | Alt - 6 | Alt - 7 | Alt - 8 | Alt - 9 | Alt - 10 | Alt - 11 | Alt - 12 | Alt - 13 | Alt - 14 | Alt - 15 | Alt - 16 | Alt - 17 | Alt - 18 | Alt - 19 | Alt - 20
| Choose Combination to be added/ subtracted | None | Alt - 1: Add; Alt - 18: 1
| Choose Combination to be added/ subtracted | None | Alt - 1: Add; Alt - 18: 1
| Choose Combination to be added/ subtracted | None | Alt - 1: Add
None
Combination-1
| Total Hard cost of the Configuration chosen (INR Crores) | 65.117 | Alt - 18: Combination-2
Combination-3
Combination-4
Combination-5
Combination-6
Taxes and Duties | bar: Alt - 1 to Alt - 11
|  | Present | Alt - 1: Updated
| Excise Duty (on Ex-Works Price) | 8% | bar: Alt - 1
| Cess on ED (on Excise Duty) | 3% | bar: Alt - 1
| Central Sales Tax (on Ex-Works Price + ED + Cess) | 2% | bar: Alt - 1
| ED+ Cess | 8.24%
| Central sales Tax | 2.165%
| Total | 10.4%

## Indices
CERC
Capital Cost Benchmarking
| S.No. | Particulars | Units | 2002-01-01 | 2002-02-01 | 2002-03-01 | 2002-04-01 | 2002-05-01 | 2002-06-01 | 2002-07-01 | 2002-08-01 | 2002-09-01 | 2002-10-01 | 2002-11-01 | 2002-12-01 | 2003-01-01 | 2003-02-01 | 2003-03-01 | 2003-04-01 | 2003-05-01 | 2003-06-01 | 2003-07-01 | 2003-08-01 | 2003-09-01 | 2003-10-01 | 2003-11-01 | 2003-12-01 | 2004-01-01 | 2004-02-01 | 2004-03-01 | 2004-04-01 | 2004-05-01 | 2004-06-01 | 2004-07-01 | 2004-08-01 | 2004-09-01 | 2004-10-01 | 2004-11-01 | 2004-12-01 | 2005-01-01 | 2005-02-01 | 2005-03-01 | 2005-04-01 | 2005-05-01 | 2005-06-01 | 2005-07-01 | 2005-08-01 | 2005-09-01 | 2005-10-01 | 2005-11-01 | 2005-12-01 | 2006-01-01 | 2006-02-01 | 2006-03-01 | 2006-04-01 | 2006-05-01 | 2006-06-01 | 2006-07-01 | 2006-08-01 | 2006-09-01 | 2006-10-01 | 2006-11-01 | 2006-12-01 | 2007-01-01 | 2007-02-01 | 2007-03-01 | 2007-04-01 | 2007-05-01 | 2007-06-01 | 2007-07-01 | 2007-08-01 | 2007-09-01 | 2007-10-01 | 2007-11-01 | 2007-12-01 | 2008-01-01 | 2008-02-01 | 2008-03-01 | 2008-04-01 | 2008-05-01 | 2008-06-01 | 2008-07-01 | 2008-08-01 | 2008-09-01 | 2008-10-01 | 2008-11-01 | 2008-12-01 | 2009-01-01 | 2009-02-01 | 2009-03-01 | 2009-04-01 | 2009-05-01 | 2009-06-01 | 2009-07-01 | 2009-08-01 | 2009-09-01 | 2009-10-01 | 2009-11-01 | 2009-12-01 | 2010-01-01 | 2010-02-01 | 2010-03-01 | 2010-04-01 | 2010-05-01 | 2010-06-01 | 2010-07-01 | 2010-08-01 | 2010-09-01 | 2010-10-01 | 2010-11-01 | 2010-12-01 | 2011-01-01 | 2011-02-01 | 2011-03-01 | 2011-04-01 | 2011-05-01 | 2011-06-01 | 2011-07-01 | 2011-08-01 | 2011-09-01 | 2011-10-01 | 2011-11-01 | 2011-12-01 | 2012-01-01 | 2012-02-01 | 2012-03-01 | 2012-04-01 | 2012-05-01 | 2012-06-01 | 2012-07-01 | 2012-08-01 | 2012-09-01 | 2012-10-01 | 2012-11-01 | 2012-12-01 | 2013-01-01 | 2013-02-01 | 2013-03-01 | 2013-04-01 | 2013-05-01 | 2013-06-01 | 2013-07-01 | 2013-08-01 | 2013-09-01 | 2013-10-01 | 2013-11-01 | 2013-12-01 | 2014-01-02
| 1 | Power Transformer
| a) | Copper | INR/ MT | 117662 | [18 empty] | 105116 | [6 empty] | 161583 |  |  |  | 150346 | 151962 | 156101 | 156101 | 162132 |  | 161959 |  |  |  | 155105 |  |  | 169400 | 183947 |  |  |  | 234065 | 246882 | 246187 | 321694 | 405017 | 360240 | 396727 | 396250 | 388127 | 377445 | 349767 | 331319 | 321137 | 266730 | 268199 | 300799 | 341326 | 331023 | 343064 | 310398 | 327855 | 350128 | 340897 | 291788 | 271169 | 298979 | 384365 | 356028 | 374688 | 378574 | 378065 | 379097 | 342410 | 349353 | 254789 | 201489 | 155954 | 166808 | 175396 | 207578 | 232254 | 240138 | 258059 | 271982 | 314505 | 308032 | 319423 | 326293 | 343582
| b) | Electrical Steel sheet -CRGO | INR/ MT | 125048 | [18 empty] | 82245 | [6 empty] | 84522 |  |  |  | 96618 | 82864 | 84681 | 84681 | 86634 |  | 101372 |  |  |  | 161048 |  |  | 188786 | 212825 |  |  |  | 200074 | 195894 | 194855 | 221331 | 204827 | 203822 | 212009 | 210100 | 209593 | 200334 | 203675 | 198712 | 200218 | 195011 | 196183 | 191168 | 182565 | 185109 | 219073 | 198404 | 209701 | 191920 | 192092 | 195575 | 188296 | 194326 | 231172 | 195118 | 203869 | 212968 | 215227 | 225373 | 229721 | 243082 | 238764 | 230946 | 250205 | 228507 | 237253 | 222515 | 219799 | 186754 | 187491 | 182536 | 170393 | 164804 | 162203 | 157341 | 152995
| c) | Iron & Steel | Index No | 137.6 | [18 empty] | 166.1 | [6 empty] | 198.7 |  |  |  | 239.8 | 242.9 | 237.2 | 237.2 | 237.2 |  | 239.9 |  |  |  | 258.8 |  |  | 256.3 | 259.7 |  |  |  | 257.9 | 256.9 | 233.4 | 243.3 | 226.2 | 243.3 | 243.9 | 243.4 | 250.8 | 253.5 | 254.9 | 258.9 | 259.3 | 259.2 | 259.9 | 260.1 | 261.2 | 266.2 | 268.3 | 276.7 | 276.7 | 217.22 | 276.7 | 277.3 | 277.9 | 280.1 | 280.6 | 280 | 287.4 | 357.1 | 354.6 | 357.9 | 353.67 | 348.92 | 341.61 | 338.67 | 330.6 | 322.7 | 319.1 | 286.1 | 289 | 286 | 286.2 | 286.7 | 286.4 | 296.4 | 288.1 | 291.4 | 291.3
| d) | Insulating Material | INR/ Kg | 185.45 | [18 empty] | 185.45 | [6 empty] | 310.82 |  |  |  | 309.36 | 287.76 | 286.59 | 286.59 | 290.5 |  | 346.69 |  |  |  | 289.25 |  |  | 251.56 | 301.15 |  |  |  | 286.83 | 288.92 | 300.68 | 309.05 | 308.45 | 307,52 | 306.86 | 303.78 | 302.1 | 290.46 | 287.38 | 286.94 | 286.94 | 286.94 | 286.94 | 282.48 | 282.48 | 282.48 | 331.53 | 275.4 | 305.11 | 281.76 | 281.17 | 286.55 | 302.69 | 311.55 | 365.31 | 365 | 373.71 | 374.56 | 389.66 | 411.88 | 406.98 | 399.71 | 392.28 | 390.17 | 387.81 | 363.11 | 359.59 | 384.24 | 373.24 | 381.53 | 392.25 | 407.77 | 408.76 | 408.76 | 403.14 | 403.35 | 405.91
| e) | Transformer Oil | INR/ KL | 35513 | [18 empty] | 39098 | [6 empty] | 24797 |  |  |  | 26266 | 27305 | 27070 | 27070 | 28387 |  | 28160 |  |  |  | 25774 |  |  | 26444 | 32498 |  |  |  | 34017 | 34017 | 36127 | 38018 | 38018 | 40350 | 40655 | 42602 | 42241 | 43946 | 41113 | 38995 | 38779 | 38562 | 38661 | 38183 | 36487 | 35573 | 35269 | 32484 | 36007 | 49950 | 35827 | 35827 | 36319 | 38599 | 39304 | 39304 | 40182 | 45215 | 49358 | 56272 | 59080 | 56642 | 54287 | 53145 | 52986 | 49375 | 46625 | 46250 | 45500 | 44125 | 44125 | 47300 | 47250 | 50950 | 50375 | 49625 | 50625
| f) | Labour | Index No. | 111.9552 | [18 empty] | 117.3648 | [6 empty] | 118.5408 |  |  |  | 121.5984 | 122.7744 | 123.0096 | 123.0096 | 123.7152 |  | 123.7152 |  |  |  | 123.9504 |  |  | 127.008 | 127.4784 |  |  |  | 130.0656 | 129.1248 | 129.5952 | 130.7712 | 130.7712 | 130.7712 | 131.712 | 133.8288 | 135.0048 | 135.0048 | 136.1808 | 138.2976 | 138.3 | 138.3 | 138.3 | 139.3889 | 138.3 | 139.3889 | 132.0093 | 133.0094 | 133.0094 | 144.8832 | 144.8338 | 145.9228 | 145.9228 | 145.9228 | 138.0097 | 147 | 149.19 | 150.28 | 151.37 | 152.46 | 147.25 | 149.3073 | 150.337 | 150.337 | 147.0093 | 148 | 148 | 150.64 | 151 | 153 | 160 | 162 | 163 | 165 | 168 | 168
| 2 | LT Transformer | [34 empty] | 286.59
| a) | Copper | INR/ MT | 117662 | [18 empty] | 105116 | [6 empty] | 161583 |  |  |  | 150346 | 151962 | 156101 | 156101 | 162132 |  | 161959 |  |  |  | 155105 |  |  | 169400 | 183947 |  |  |  | 234065 | 246882 | 246187 | 321694 | 405017 | 360240 | 396727 | 396250 | 388127 | 377445 | 349767 | 331319 | 321137 | 266730 | 268199 | 300799 | 341326 | 331023 | 343064 | 310398 | 327855 | 350128 | 340897 | 291788 | 271169 | 298979 | 384365 | 356028 | 374688 | 378574 | 378065 | 379097 | 342410 | 349353 | 254789 | 201489 | 155954 | 166808 | 175396 | 207578 | 232254 | 240138 | 258059 | 271982 | 314505 | 308032 | 319423 | 326293 | 343582
| b) | Electrical Steel sheet -CRGO | INR/ MT | 125048 | [18 empty] | 82245 | [6 empty] | 84522 |  |  |  | 96618 | 82864 | 84681 | 84681 | 86634 |  | 101372 |  |  |  | 161048 |  |  | 188786 | 212825 |  |  |  | 200074 | 195894 | 194855 | 221331 | 204827 | 203822 | 212009 | 210100 | 209593 | 200334 | 203675 | 198712 | 200218 | 195011 | 196183 | 191168 | 182565 | 185109 | 219073 | 198404 | 209701 | 215120 | 192092 | 195575 | 188296 | 194326 | 231172 | 195118 | 203689 | 212968 | 215227 | 225373 | 229721 | 243082 | 238764 | 230946 | 250205 | 228507 | 237253 | 222515 | 219799 | 186754 | 187491 | 182536 | 170393 | 164804 | 162203 | 157341 | 152995
| c) | Iron & Steel | Index No | 137.6 | [18 empty] | 166.1 | [6 empty] | 198.7 |  |  |  | 239.8 | 242.9 | 237.2 | 237.2 | 237.2 |  | 239.9 |  |  |  | 258.8 |  |  | 256.3 | 259.7 |  |  |  | 257.9 | 256.9 | 233.4 | 243.3 | 226.2 | 243.3 | 243.9 | 243.4 | 250.8 | 253.5 | 254.9 | 258.9 | 259.3 | 259.2 | 259.9 | 260.1 | 261.2 | 266.2 | 268.3 | 276.7 | 276.7 | 217.22 | 276.7 | 277.3 | 277.9 | 280.1 | 280.6 | 280 | 387.4 | 357.1 | 354.6 | 357.9 | 353.67 | 348.92 | 341.61 | 338.67 | 330.6 | 322.7 | 319.1 | 286.1 | 289 | 286 | 286.2 | 286.7 | 286.4 | 296.4 | 288.1 | 291.4 | 291.3
| d) | Insulating Material | INR/ Kg | 185.45 | [18 empty] | 185.45 | [6 empty] | 310.82 |  |  |  | 309.36 | 287.76 | 286.59 | 286.59 | 290.5 |  | 346.69 |  |  |  | 289.25 |  |  | 251.56 | 301.15 |  |  |  | 286.83 | 288.92 | 300.68 | 309.05 | 308.45 | 307.52 | 306.86 | 303.78 | 302.1 | 290.46 | 287.38 | 286.94 | 286.94 | 286.94 | 286.94 | 282.48 | 282.48 | 282.48 | 331.53 | 275.4 | 305.11 | 281.76 | 281.17 | 286.55 | 302.69 | 311.55 | 375.31 | 365 | 373.31 | 374.56 | 389.66 | 411.88 | 406.98 | 399.71 | 392.28 | 390.17 | 387.81 | 363.11 | 359.59 | 384.24 | 373.24 | 381.53 | 392.25 | 407.77 | 408.76 | 408.76 | 403.14 | 403.35 | 405.91
| e) | Transformer Oil | INR/ KL | 35513 | [18 empty] | 39098 | [6 empty] | 24797 |  |  |  | 26266 | 27305 | 27070 | 27070 | 28387 |  | 28160 |  |  |  | 25774 |  |  | 26444 | 32498 |  |  |  | 34017 | 34017 | 36127 | 38018 | 38018 | 40350 | 40655 | 42602 | 42241 | 43946 | 41113 | 38995 | 38779 | 38562 | 38661 | 38183 | 36487 | 35573 | 35704 | 35269 | 37131 | 49950 | 35827 | 35827 | 36319 | 38599 | 39304 | 39304 | 40182 | 45215 | 49538 | 56272 | 59080 | 56642 | 54287 | 53145 | 52986 | 49375 | 46625 | 46250 | 45500 | 44125 | 44125 | 47300 | 47250 | 50950 | 50375 | 49625 | 50625
| f) | Labour | Index No. | 111.9552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 117.3648 |  | 0 | 0 | 0 | 0 | 0 | 118.5408 | 0 |  | 0 | 121.5984 | 122.7744 | 123.0096 | 123.0096 | 123.7152 | 0 | 123.7152 | 0 | 0 | 0 | 123.9504 | 0 | 0 | 127.008 | 127.4784 | 0 | 0 | 0 | 130.0656 | 129.1248 | 129.5952 | 130.7712 | 130.7712 | 130.7712 | 131.712 | 133.8288 | 135.0048 | 135.0048 | 136.1808 | 138.2976 | 138.3 | 138.3 | 138.3 | 139.3889 | 138.3 | 139.3889 | 132.0093 | 133.0094 | 133.0094 | 144.8832 | 144.8338 | 145.9228 | 145.9228 | 145.9228 | 138.0097 | 147 | 149.19 | 150.28 | 151.3677 | 152.46 | 147.25 | 149.3073 | 150.337 | 150.337 | 147.0093 | 148 | 148 | 150.64 | 151 | 153 | 160 | 162 | 163 | 165 | 168 | 168
| 3 | Circuit Breaker
| a) | Iron & Steel | Index No. | 137.6 | [18 empty] | 166.1 | [6 empty] | 198.7 |  |  |  |  | 242.9 | 237.2 |  | 237.2 | [5 empty] | 258.8 |  |  | 256.3 |  |  |  |  | 257.9 | 256.9 | 233.4 | 243.3 | 226.2 | 243.3 | 243.9 | 243.4 | 250.8 | 253.5 | 254.9 | 258.9 | 259.3 | 259.2 | 259.9 | 260.1 | 261.2 | 266.2 | 267.2 | 268.7 | 268.3 | 217.22 | 276.7 | 277.3 | 277.9 | 280.13 | 280.6 | 280.6 | 287.4 | 357.1 | 354.6 | 357 | 353.67 | 348.92 | 341.61 | 338.67 | 330.6 | 322.7 | 319.1 | 286.1 | 289 | 286 | 286.2 | 286.7 | 286.4 | 296.4 | 288.1 | 291.4 | 291.3
| b) | Copper | INR/ MT | 117662 | [18 empty] | 121706 | [6 empty] | 180263 |  |  |  |  | 170202 | 171962 |  | 171962 | [5 empty] | 174024 |  |  | 196067 |  |  |  |  | 245956 | 246882 | 246187 | 321694 | 405017 | 360240 | 396727 | 396250 | 388127 | 377445 | 349767 | 331319 | 321137 | 266730 | 268199 | 300799 | 341326 | 331023 | 327276 | 343064 | 328486 | 350128 | 299451 | 283695 | 302578 | 340650 | 384365 | 3,56,028 | 374688 | 378574 | 378065 | 379097 | 342410 | 349353 | 254789 | 201489 | 155954 | 166808 | 175396 | 207578 | 232254 | 240138 | 258059 | 271982 | 314505 | 308032 | 319423 | 326293 | 343582
| c) | Aluminium | INR/ MT | 104050 | [18 empty] | 107950 | [6 empty] | 109025 |  |  |  |  | 114325 | 117325 |  | 117325 | [5 empty] | 124650 |  |  | 117050 |  |  |  |  | 140300 | 146300 | 147800 | 148800 | 161800 | 161800 | 153300 | 153800 | 155300 | 154800 | 166300 | 162300 | 166300 | 162900 | 162900 | 160400 | 159400 | 155900 | 152900 | 155900 | 148900 | 145900 | 147400 | 144900 | 141400 | 143400 | 141317 | 1,63,400 | 167400 | 175400 | 174400 | 178400 | 167410 | 159465 | 151836 | 141398 | 131900 | 128400 | 128400 | 128400 | 131400 | 126900 | 132400 | 144650 | 150650 | 146650 | 148150 | 151150 | 162650
| d) | Epoxy Resin | INR/ Kg | 168 | [18 empty] | 168 | [6 empty] | 168 |  |  |  |  | 168 | 168 |  | 168 | [5 empty] | 168 |  |  | 168 |  |  |  |  | 168 | 168 | 168 | 168 | 168 | 168 | 180 | 180 | 180 | 180 | 180 | 198 | 198 | 198 | 198 | 198 | 198 | 198 | 198 | 198 | 198 | 198 | 198 | 198 | 198 | 198 | 198 | 198 | 198 | 198 | 198 | 198 | 198 | 198 | 198 | 198 | 198 | 198 | 188 | 188 | 188 | 188 | 188 | 188 | 188 | 188 | 188 | 188 | 188
| e) | Labour | Index No. | 111.9552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 117.3648 |  | 0 | 0 | 0 | 0 | 0 | 118.5408 | 0 |  | 0 | 121.5984 | 122.7744 | 123.0096 |  | 123.7152 | 0 | 123.7152 | 0 | 0 | 0 | 123.9504 | 0 | 0 | 127.008 | 127.4784 | 0 | 0 | 0 | 130.0656 | 129.1248 | 129.5952 | 130.7712 | 130.7712 | 130.7712 | 131.712 | 133.8288 | 135.0048 | 135.0048 | 136.1808 | 138.2976 | 138.3 | 138.3 | 138.3 | 139.3889 | 138.3 | 139.3889 | 132.0093 | 133.0094 | 133.0094 | 144.8832 | 144.8338 | 145.9228 | 145.9228 | 145.9228 | 138.0097 | 147 | 149.19 | 150.28 | 151.37 | 152.46 | 147.25 | 149.3073 | 150.337 | 150.337 | 147.0093 | 148 | 148 | 150.64 | 151 | 153 | 160 | 162 | 163 | 165 | 168 | 168
| 4 | Current Transformer and Voltage Transformer
| a) | Index INSLR | Index No | 116.16 | [18 empty] | 122.14 | [6 empty] | 131.81 |  |  |  |  | 138.48 | 142.91 |  | 145.26 | [5 empty] | 173.25 |  |  | 181.11 |  |  |  |  | 136.69 | 136.24 | 134.1 | 133.93 | 134.42 | 137.6 | 138.99 | 139.25 | 141.91 | 142.76 | 143.83 | 144.08 | 143.74 | 142.89 | 144.33 | 143.95 | 143.74 | 144.43 | 144.78 | 144.88 | 144.72 | 144.79 | 145.71 | 146.4 | 148.13 | 148.18 | 148.21 | 148.21 | 150.71 | 159.36 | 160.11 | 167.71 | 170.33 | 171.24 | 168.45 | 164.89 | 161.94 | 157.02 | 159.87 | 150.87 | 150.64 | 150.7 | 153.18 | 153.63 | 156.06 | 157.95 | 157.56 | 158.03 | 159.31
| b) | Iron & Steel | Index No | 137.6 | [18 empty] | 166.1 | [6 empty] | 198.7 |  |  |  |  | 242.9 | 237.2 |  | 237.2 | [5 empty] | 258.8 |  |  | 256.3 |  |  |  |  | 257.9 | 256.9 | 233.4 | 243.3 | 226.2 | 243.3 | 243.9 | 243.4 | 250.8 | 253.5 | 254.9 | 258.9 | 259.3 | 259.2 | 259.9 | 260.1 | 261.2 | 266.2 | 267.2 | 268.7 | 268.3 | 217.22 | 276.7 | 277.3 | 277.9 | 280.13 | 280.6 | 280.6 | 287.4 | 357.1 | 354.6 | 357.9 | 353.67 | 348.92 | 341.61 | 338.67 | 330.6 | 322.7 | 319.1 | 286.1 | 289 | 286 | 286.2 | 286.7 | 286.4 | 296.4 | 288.1 | 291.4 | 291.3
| c) | Transformer Oil | INR/ KL | 35513 | [18 empty] | 39098 | [6 empty] | 40560 |  |  |  |  | 43210 | 43435 |  | 44335 | [5 empty] | 39160 |  |  | 39923 |  |  |  |  | 34017 | 34017 | 36127 | 38018 | 38018 | 40350 | 40655 | 42602 | 42241 | 43946 | 41113 | 38995 | 38779 | 38562 | 38661 | 38183 | 36487 | 35573 | 35704 | 35269 | 37131 | 49950 | 35827 | 35827 | 36319 | 38599 | 39304 | 39304 | 40182 | 45215 | 49538 | 56272 | 59080 | 56642 | 54287 | 53145 | 52986 | 49375 | 46625 | 46250 | 45500 | 44125 | 44125 | 47300 | 47250 | 50950 | 50375 | 49625 | 50625
| d) | Index No.for Insulator | Index No | 116.16 | [18 empty] | 122.14 | [6 empty] | 131.81 |  |  |  |  | 138.48 | 142.91 |  | 145.26 | [5 empty] | 173.25 |  |  | 181.11 |  |  |  |  | 136.69 | 136.24 | 134.1 | 133.93 | 134.42 | 137.6 | 138.99 | 139.25 | 141.91 | 142.76 | 143.83 | 144.08 | 143.74 | 142.89 | 144.33 | 143.95 | 143.74 | 144.43 | 144.78 | 144.88 | 144.72 | 144.79 | 145.71 | 146.4 | 148.13 | 148.18 | 148.21 | 148.21 | 150.71 | 159.36 | 160.11 | 167.71 | 170.33 | 171.24 | 168.45 | 164.89 | 161.94 | 157.02 | 159.87 | 150.87 | 150.64 | 150.7 | 153.18 | 153.63 | 156.06 | 157.95 | 157.56 | 158.03 | 159.31
| e) | Electrical Steel sheet -CRGO | INR/ MT | 125048 | [18 empty] | 82245 | [6 empty] | 84522 |  |  |  |  | 82864 | 84681 |  | 86634 | [5 empty] | 161048 |  |  | 188786 |  |  |  |  | 200074 | 195894 | 194855 | 198351 | 204827 | 203822 | 212009 | 210100 | 209593 | 200334 | 203675 | 198712 | 200218 | 195011 | 196183 | 191168 | 182565 | 185109 | 195331 | 190181 | 190143 | 215120 | 192092 | 195575 | 188296 | 194326 | 231172 | 1,95,118. | 2,03,869 | 212968 | 215227 | 225373 | 229721 | 243082 | 248367 | 249862 | 250205 | 228507 | 237253 | 222515 | 219799 | 186754 | 187491 | 182536 | 170393 | 164804 | 162203 | 157341 | 152995
| f) | Copper | INR/ MT | 117662 | [18 empty] | 121706 | [6 empty] | 161583 |  |  |  |  | 170202 | 171962 |  | 177245 | [5 empty] | 174024 |  |  | 196067 |  |  |  |  | 245956 | 246882 | 246187 | 321694 | 405017 | 360240 | 396727 | 396250 | 388127 | 377445 | 349767 | 331319 | 321137 | 266730 | 268199 | 300799 | 341326 | 331023 | 327276 | 343064 | 328486 | 343215 | 299451 | 283695 | 302578 | 340650 | 384365 | 3,56,028 | 374688 | 378574 | 378065 | 3,79,097 | 342410 | 349353 | 254789 | 201489 | 155954 | 166808 | 175396 | 207578 | 232254 | 240138 | 258090 | 271982 | 314505 | 308032 | 319423 | 326293 | 343582
| g) | Aluminium | INR/ MT | 104050 | [18 empty] | 107950 | [6 empty] | 109025 |  |  |  |  | 114325 | 117325 |  | 117325 | [5 empty] | 124650 |  |  | 117050 |  |  |  |  | 140300 | 146300 | 147800 | 148800 | 161800 | 161800 | 153300 | 153800 | 155300 | 154800 | 166300 | 162300 | 166300 | 162900 | 162900 | 160400 | 159400 | 155900 | 152900 | 155900 | 148900 | 145900 | 147400 | 144900 | 141400 | 143400 | 141317 | 1,63,400 | 1,67,400 | 175400 | 174400 | 1,78,400 | 167410 | 159465 | 151836 | 141398 | 131900 | 128400 | 128400 | 128400 | 131400 | 126900 | 132400 | 144650 | 150650 | 146650 | 148150 | 151150 | 162650
| h) | Epoxy Resin | INR/ Kg | 168 | [18 empty] | 168 | [6 empty] | 168 |  |  |  |  | 168 | 168 |  | 168 | [5 empty] | 168 |  |  | 168 |  |  |  |  | 168 | 168 | 168 | 168 | 168 | 168 | 180 | 180 | 180 | 180 | 180 | 198 | 198 | 198 | 198 | 198 | 198 | 198 | 198 | 198 | 198 | 198 | 198 | 198 | 198 | 198 | 198 | 198 | 198 | 198 | 198 | 198 | 198 | 198 | 198 | 198 | 198 | 198 | 188 | 188 | 188 | 188 | 188 | 188 | 188 | 188 | 188 | 188 | 188
| i) | Labour | Index No | 111.9552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 117.3648 |  | 0 | 0 | 0 | 0 | 0 | 118.5408 | 0 |  | 0 | 121.5984 | 122.7744 | 123.0096 |  | 123.7152 | 0 | 123.7152 | 0 | 0 | 0 | 123.9504 | 0 | 0 | 127.008 | 127.4784 | 0 | 0 | 0 | 130.0656 | 129.1248 | 129.5952 | 130.7712 | 130.7712 | 130.7712 | 131.712 | 133.8288 | 135.0048 | 135.0048 | 136.1808 | 138.2976 | 138.3 | 138.3 | 138.3 | 139.3889 | 138.3 | 139.3889 | 132.0093 | 133.0094 | 133.0094 | 144.8832 | 144.8338 | 145.9228 | 145.9228 | 145.9228 | 138.0097 | 147 | 149.1897 | 150.28 | 151.37 | 152.4566 | 147.2479 | 149.3073 | 150.337 | 150.337 | 147.0093 | 148 | 148 | 150.64 | 151 | 153 | 160 | 162 | 163 | 165 | 168 | 168
| 5 | Isolator
| a) | Iron & Steel | Index No | 137.6 | [18 empty] | 166.1 | [6 empty] | 198.7 |  |  |  |  | 242.9 | 237.2 |  | 237.2 | [5 empty] | 258.8 |  |  | 256.3 |  |  |  |  | 257.9 | 256.9 | 233.4 | 243.3 | 226.2 | 243.3 | 243.9 | 243.4 | 250.8 | 253.5 | 254.9 | 258.9 | 259.3 | 259.2 | 259.9 | 260.1 | 261.2 | 266.2 | 267.2 | 268.7 | 268.3 | 217.22 | 276.7 | 277.3 | 277.9 | 280.13 | 280.6 | 280.6 | 287.4 | 357.1 | 354.6 | 357.9 | 353.67 | 348.92 | 341.61 | 338.67 | 330.6 | 322.7 | 319.1 | 286.1 | 289 | 286 | 286.2 | 286.7 | 286.4 | 296.4 | 288.1 | 291.4 | 291.3
| b) | Copper | INR/ MT | 117662 | [18 empty] | 121706 | [6 empty] | 180263 |  |  |  |  | 170202 | 171962 |  | 177245 | [5 empty] | 174024 |  |  | 196067 |  |  |  |  | 245956 | 246882 | 246187 | 321694 | 405017 | 360240 | 396727 | 396250 | 388127 | 377445 | 349767 | 331319 | 321137 | 266730 | 268199 | 300799 | 341326 | 331023 | 327276 | 343064 | 328486 | 350128 | 299451 | 283695 | 302578 | 340650 | 384365 | 3,56,028 | 374688 | 378574 | 3,78,065 | 3,79,097 | 342410 | 349353 | 254789 | 201489 | 155954 | 166808 | 175396 | 207578 | 232254 | 240138 | 258090 | 271982 | 314505 | 308032 | 319423 | 326293 | 343582
| c) | Alluminium | INR/ MT | 104050 | [18 empty] | 107950 | [6 empty] | 109025 |  |  |  |  | 114325 | 117325 |  | 117325 | [5 empty] | 124650 |  |  | 117050 |  |  |  |  | 140300 | 146300 | 147800 | 148800 | 161800 | 161800 | 153300 | 153800 | 155300 | 154800 | 166300 | 162300 | 166300 | 162900 | 162900 | 160400 | 159400 | 155900 | 152900 | 155900 | 148900 | 145900 | 147400 | 144900 | 141400 | 143400 | 141317 | 1,63,400 | 1,67,400 | 175400 | 1,74,400 | 1,78,400 | 167400 | 159465 | 151836 | 141398 | 131900 | 128400 | 128400 | 128400 | 131400 | 126900 | 132400 | 144650 | 150650 | 146650 | 148150 | 151150 | 162650
| d) | Epoxy Resin | INR/ Kg | 168 | [18 empty] | 168 | [6 empty] | 168 |  |  |  |  | 522 | 168 |  | 168 | [5 empty] | 168 |  |  | 168 |  |  |  |  | 168 | 168 | 168 | 168 | 168 | 168 | 180 | 180 | 180 | 180 | 180 | 198 | 198 | 198 | 198 | 198 | 198 | 198 | 198 | 198 | 198 | 198 | 198 | 198 | 198 | 198 | 198 | 198 | 198 | 198 | 198 | 198 | 198 | 198 | 198 | 198 | 198 | 198 | 188 | 188 | 188 | 188 | 188 | 188 | 188 | 188 | 188 | 188 | 188
| e) | Labour | Index No. | 111.9552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 117.3648 |  | 0 | 0 | 0 | 0 | 0 | 118.5408 | 0 |  | 0 | 121.5984 | 122.7744 | 123.0096 |  | 123.7152 | 0 | 123.7152 | 0 | 0 | 0 | 123.9504 | 0 | 0 | 127.008 | 127.4784 | 0 | 0 | 0 | 130.0656 | 129.1248 | 129.5952 | 130.7712 | 130.7712 | 130.7712 | 131.712 | 133.8288 | 135.0048 | 135.0048 | 136.1808 | 138.2976 | 138.3 | 138.3 | 138.3 | 139.3889 | 138.3 | 139.3889 | 132.0093 | 133.0094 | 133.0094 | 144.8832 | 144.8338 | 145.9228 | 145.9228 | 145.9228 | 138.0097 | 147 | 149.1897 | 150.2787 | 151.3677 | 152.4566 | 147.25 | 149.3073 | 150.337 | 150.337 | 147.0093 | 148 | 148 | 150.64 | 151 | 153 | 160 | 162 | 163 | 165 | 168 | 168
| 6 | Surge Arrester
| a) | Zinc | INR/ MT | 52800 | [18 empty] | 55900 | [6 empty] | 66000 |  |  |  |  | 58600 | 57900 |  | 57900 | [5 empty] | 69900 |  |  | 66300 |  |  |  |  | 107100 | 124500 | 121500 | 140200 | 171900 | 197900 | 166200 | 175300 | 181600 | 180500 | 212300 | 228800 | 221500 | 176500 | 178000 | 160400 | 174000 | 166300 | 157800 | 163500 | 144500 | 136700 | 131100 | 111100 | 109800 | 104200 | 107300 | 107300 | 98000 | 97700 | 90300 | 88700 | 83657 | 76145 | 72134 | 68926 | 63400 | 68900 | 67900 | 80700 | 88400 | 88200 | 91000 | 98900 | 106900 | 108300 | 125900 | 123700 | 139800
| b) | Cobalt | INR/ Kg | 1268.82 | [18 empty] | 1425.14 | [6 empty] | 3317.41 |  |  |  |  | 3102.75 | 299.64 |  | 2993.64 | [5 empty] | 1938.31 |  |  | 1516.42 |  |  |  |  | 1756.49 | 1566.66 | 1436.71 | 1545.07 | 1716.5 | 1794.76 | 1698.04 | 1655.52 | 1985.91 | 2203.03 | 1996.81 | 2024.6 | 2889.92 | 2725.73 | 2762.56 | 3064.45 | 2954.22 | 2806.47 | 2665.83 | 2550.15 | 2443.39 | 2662.27 | 2764.57 | 3038.87 | 3632.43 | 4203.7 | 4570.15 | 4784.31 | 4726.05 | 4772.21 | 4495.37 | 4035.76 | 3827.61 | 33143.28 | 2892.46 | 2637.34 | 1677.63 | 2003.71 | 1748.72 | 1602.87 | 1850.25 | 1721.26 | 1642.2 | 2023.92 | 2210.95 | 2149.1 | 1946.99 | 2336.41 | 2190.66
| c) | Alluminium | INR/ MT | 104050 | [18 empty] | 107950 | [6 empty] | 109025 |  |  |  |  | 114325 | 117325 |  | 117325 | [5 empty] | 124650 |  |  | 117050 |  |  |  |  | 140300 | 146300 | 147800 | 148800 | 161800 | 161800 | 153300 | 153800 | 155300 | 154800 | 166300 | 162300 | 166300 | 162900 | 162900 | 160400 | 159400 | 155900 | 152900 | 155900 | 148900 | 145900 | 147400 | 144900 | 141400 | 143400 | 141317 | 1,63,400 | 1,67,400 | 175400 | 1,74,400 | 1,78,400 | 1,67,400 | 159465 | 151836 | 141398 | 131900 | 128400 | 128400 | 128400 | 131400 | 126900 | 132400 | 144650 | 150650 | 146650 | 148150 | 151150 | 162650
| d) | Ball clay | INR/ MT | 957.5 | [18 empty] | 942.5 | [6 empty] | 942.5 |  |  |  |  | 1217.5 | 461.45 |  | 461.45 | [5 empty] | 1575 |  |  | 1575 |  |  |  |  | 1575 | 1575 | 1575 | 1575 | 1575 | 1675 | 1725 | 1725 | 1725 | 1725 | 1725 | 1725 | 1725 | 1725 | 1725 | 1725 | 1725 | 1725 | 1725 | 1725 | 1725 | 1725 | 1725 | 1725 | 1725 | 1725 | 1725 | 1725 | 1725 | 1725 | 1725 | 1725 | 1725 | 1725 | 1846 | 1893 | 1975 | 1975 | 1975 | 2025 | 2025 | 2025 | 2275 | 2275 | 2275 | 2275 | 2275 | 2275 | 2409
| e) | Bismath | INR/ Kg | 450.12 | [18 empty] | 499 | [6 empty] | 366.67 |  |  |  |  | 462.51 | 1217.5 |  | 1217.5 | [5 empty] | 393.87 |  |  | 457.1 |  |  |  |  | 550.99 | 538.49 | 535.53 | 465.31 | 516.54 | 517.64 | 505.75 | 511.61 | 526.8 | 555.84 | 649.34 | 690.01 | 792.79 | 916.72 | 978.7 | 1108.54 | 1402.73 | 1671.45 | 1723.64 | 1658.22 | 1664.86 | 1469.7 | 1315.72 | 1272.41 | 1236.55 | 1103.05 | 1158.03 | 1416.12 | 1525.07 | 1433.9 | 1287.77 | 1158.03 | 1148.83 | 1182.67 | 1136.94 | 1185.26 | 1066.29 | 1073.42 | 1114.5 | 1086.91 | 972.94 | 873.21 | 798.12 | 763.51 | 780.47 | 982.04 | 992.73 | 951.89 | 865.03
| f) | Fuels/power | Index No | 253.2 | [18 empty] | 253.2 | [6 empty] | 253.2 |  |  |  |  | 253.2 | 253.2 |  | 253.2 | [5 empty] | 293.2 |  |  | 304 |  |  |  |  | 312.4 | 310.7 | 311 | 313.5 | 314.7 | 316.8 | 319.7 | 320.1 | 326.5 | 328.9 | 331.4 | 329.6 | 326.7 | 322.4 | 322.3 | 320.7 | 319.6 | 320.3 | 322 | 321.9 | 321.8 | 322.4 | 321.7 | 323.7 | 326.5 | 334.4 | 334.2 | 334.2 | 334.2 | 334.2 | 334.2 | 334.2 | 334.2 | 334.2 | 334.2 | 334.2 | 350.2 | 331.8 | 329.5 | 323.5 | 321 | 322.6 | 325.2 | 327.1 | 338.4 | 342.8 | 343.6 | 344.6 | 345.4
| g) | Labour | Index No | 111.9552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 117.3648 |  | 0 | 0 | 0 | 0 | 0 | 118.5408 | 0 |  | 0 | 121.5984 | 122.7744 | 123.0096 |  | 123.7152 | 0 | 123.7152 | 0 | 0 | 0 | 123.9504 | 0 | 0 | 127.008 | 127.4784 | 0 | 0 | 0 | 130.0656 | 129.1248 | 129.5952 | 130.7712 | 130.7712 | 130.7712 | 131.712 | 133.8288 | 135.0048 | 135.0048 | 136.1808 | 138.2976 | 138.3 | 138.3 | 138.3 | 139.3889 | 138.3 | 139.3889 | 132.0093 | 133.0094 | 133.0094 | 144.8832 | 144.8338 | 145.9228 | 145.9228 | 145.9228 | 138.0097 | 147 | 149.1897 | 150.2787 | 151.3677 | 152.4566 | 147.2479 | 149.3073 | 150.337 | 150.337 | 147.0093 | 148 | 148 | 150.64 | 151 | 153 | 160 | 162 | 163 | 165 | 168 | 168
| 7 | Substation Structures including bolts and Nuts
| a) | Published Price Index of Structurel Steel | Index No | 15509 | [18 empty] | 21081 | [6 empty] | 26510 |  |  |  |  | 27772 | 26510 |  | 26510 | [5 empty] | 24946 |  |  | 30019 |  |  |  |  | 22310 | 23269 | 24214 | 25444 | 24541 | 24068 | 23595 | 24257 | 25203 | 25783 | 25783 | 26729 | 26729 | 27188 | 27925 | 28680 | 28881 | 28126 | 28611 | 29237 | 29334 | 35286 | 35900 | 36245 | 37567 | 38889 | 46434 | 46434 | 46675 | 48117 | 49269 | 49632 | 49582 | 49696 | 49874 | 49963 | 50867 | 49471 | 49894 | 49766 | 49806 | 46805 | 47030 | 47030 | 47360 | 47335 | 47437 | 48047 | 49031
| b) | Published Price Index of Electrolytic Zinc | INR / MT | 52800 | [18 empty] | 55900 | [6 empty] | 66000 |  |  |  |  | 58600 | 57900 |  | 57900 | [5 empty] | 69900 |  |  | 66300 |  |  |  |  | 107100 | 124500 | 121500 | 140200 | 171900 | 197900 | 166200 | 175300 | 181600 | 180500 | 212300 | 228800 | 221500 | 176500 | 178000 | 160400 | 174000 | 166300 | 157800 | 163500 | 144500 | 136700 | 131100 | 111100 | 109800 | 104200 | 107300 | 107300 | 98000 | 97700 | 90300 | 88700 | 86400 | 82600 | 75800 | 72500 | 63400 | 68900 | 67900 | 80700 | 88400 | 88200 | 91000 | 98900 | 106900 | 108300 | 125900 | 123700 | 139800
| c) | Labour | Index No | 111.9552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 117.3648 |  | 0 | 0 | 0 | 0 | 0 | 118.5408 | 0 |  | 0 | 121.5984 | 122.7744 | 123.0096 |  | 123.7152 | 0 | 123.7152 | 0 | 0 | 0 | 123.9504 | 0 | 0 | 127.008 | 127.4784 | 0 | 0 | 0 | 130.0656 | 129.1248 | 129.5952 | 130.7712 | 130.7712 | 130.7712 | 131.712 | 133.8288 | 135.0048 | 135.0048 | 136.1808 | 138.2976 | 138.3 | 138.3 | 138.3 | 139.3889 | 138.3 | 139.3889 | 132.0093 | 133.0094 | 133.0094 | 144.8832 | 144.8338 | 145.9228 | 145.9228 | 145.9228 | 138.0097 | 147 | 149.1897 | 150.2787 | 151.3677 | 152.4566 | 147.2479 | 149.3073 | 150.337 | 150.337 | 147.0093 | 148 | 148 | 150.64 | 151 | 153 | 160 | 162 | 163 | 165 | 168 | 168
| 8 | Index INSLR |  | 116.16 | [18 empty] | 122.14 | [6 empty] | 131.81 |  |  |  |  | 138.48 | 142.91 |  | 142.91 | [5 empty] | 173.25 |  |  | 181.11 |  |  |  |  | 136.69 | 136.24 | 134.1 | 133.93 | 134.42 | 137.6 | 138.99 | 139.25 | 141.91 | 142.76 | 143.83 | 144.08 | 143.74 | 142.89 | 144.33 | 143.95 | 143.74 | 144.43 | 144.78 | 144.88 | 144.72 | 144.79 | 145.71 | 146.4 | 148.13 | 148.18 | 148.21 | 148.21 | 150.71 | 159.36 | 160.11 | 167.71 | 170.33 | 171.24 | 168.45 | 164.89 | 161.94 | 157.02 | 159.87 | 150.87 | 150.64 | 150.7 | 153.18 | 153.63 | 156.06 | 157.95 | 157.56 | 158.03 | 159.31
| a) | Transformer Oil | INR/ KL | 35153 | [18 empty] | 107950 | [6 empty] | 109025 |  |  |  |  | 114325 | 27076 |  | 27076 | [5 empty] | 39160 |  |  | 39923 |  |  |  |  | 34017 | 34017 | 36127 | 38018 | 38018 | 40350 | 40655 | 42602 | 42241 | 43946 | 41113 | 38995 | 38779 | 38562 | 38661 | 38183 | 36487 | 35573 | 35704 | 35269 | 37131 | 49950 | 35827 | 35827 | 36319 | 38599 | 39304 | 39304 | 40182 | 45215 | 49538 | 56272 | 59080 | 56642 | 54287 | 53145 | 52986 | 49375 | 46625 | 46250 | 45500 | 44125 | 44125 | 47300 | 47250 | 50950 | 50375 | 49625 | 50625
| b) | Labour | Index No | 111.9552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 117.3648 |  | 0 | 0 | 0 | 0 | 0 | 118.5408 | 0 |  | 0 | 121.5984 | 122.7744 | 123.0096 |  | 123.7152 | 0 | 123.7152 | 0 | 0 | 0 | 123.9504 | 0 | 0 | 127.008 | 127.4784 | 0 | 0 | 0 | 130.0656 | 129.1248 | 129.5952 | 130.7712 | 130.7712 | 130.7712 | 131.712 | 133.8288 | 135.0048 | 135.0048 | 136.1808 | 138.2976 | 138.3 | 138.3 | 138.3 | 139.3889 | 138.3 | 139.3889 | 132.0093 | 133.0094 | 133.0094 | 144.8832 | 144.8338 | 145.9228 | 145.9228 | 145.9228 | 138.0097 | 147 | 149.1897 | 150.2787 | 151.3677 | 152.4566 | 147.2479 | 149.3073 | 150.337 | 150.337 | 147.0093 | 148 | 148 | 150.64 | 151 | 153 | 160 | 162 | 163 | 165 | 168 | 168
| 9 | PVC/XLPE Insulated power and control cables |  | 0 | [18 empty] | 0
| a) | PVC Compound | INR / MT | 53200 | [18 empty] | 58200 | [6 empty] | 63200 |  |  |  |  | 68000 | 76000 |  | 76000 | [5 empty] | 73250 |  |  | 71250 |  |  |  |  | 77250 | 77250 | 77250 | 77250 | 73500 | 73500 | 74750 | 80750 | 84000 | 84000 | 82000 | 82750 | 83750 | 84000 | 84000 | 82650 | 83650 | 83650 | 83650 | 86000 | 89000 | 87000 | 87000 | 87500 | 87500 | 88000 | 89000 | 89000 | 91000 | 92000 | 97000 | 97000 | 97000 | 95000 | 92650 | 85280 | 80250 | 83000 | 84000 | 84500 | 84500 | 84500 | 87000 | 88000 | 91500 | 89000 | 89000 | 90500 | 92000
| b) | Metal | INR / MT | 0 | [18 empty] | 0 | [6 empty] | 0 |  |  |  |  | 0 | 0 |  | 0 | [5 empty] | 0 |  |  | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58000 | 70200 | 63900 | 78600 | 89100 | 86100 | 96200 | 102100 | 114800 | 121700 | 125400 | 127200 | 128900
| c) | Aluminium | INR / MT | 68450 | [18 empty] | 89617 | [6 empty] | 97867 |  |  |  |  | 100433 | 100433 |  | 100433 | [5 empty] | 103083 |  |  | 102267 |  |  |  |  | 123200 | 131133 | 128567 | 132733 | 161800 | 161800 | 153300 | 153800 | 155300 | 154800 | 166300 | 162300 | 147900 | 144500 | 144500 | 142167 | 137167 | 133000 | 130000 | 131667 | 125333 | 112467 | 147400 | 144900 | 141400 | 143400 | 141317 | 1,63,400 | 1,67,400 | 1,75,400 | 1,74,400 | 1,78,400 | 1,67,400 | 159465 | 151836 | 141398 | 131900 | 104150 | 104150 | 104150 | 104150 | 104267 | 105933 | 113433 | 123267 | 121600 | 121933 | 124933 | 137433
| d) | Copper | INR / MT | 120215 | [18 empty] | 120620 | [6 empty] | 185582 |  |  |  |  | 175225 | 177037 |  | 177037 | [5 empty] | 179161 |  |  | 201855 |  |  |  |  | 253217 | 265322 | 267517 | 335829 | 409628 | 374811 | 404717 | 404230 | 395943 | 385046 | 356811 | 337991 | 287323 | 279653 | 315666 | 361752 | 346886 | 337667 | 356255 | 340050 | 341598 | 350128 | 299451 | 283695 | 302578 | 340650 | 384365 | 3,56,028 | 3,74,688 | 3,78,574 | 3,78,065 | 3,79,097 | 3,42,410 | 3,49,353 | 254789 | 201489 | 185521 | 192169 | 222863 | 254794 | 255759 | 274252 | 276648 | 335659 | 337892 | 330450 | 399607 | 361737 | 377834
| e) | weight in MT of metal KM(Size wise) |  | 0 | [18 empty] | 0 | [6 empty] | 0 |  |  |  |  | 0 | 0 |  | 0 | [5 empty] | 0 |  |  | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| f) | IOC _HST basic ceiling selling price ex -refinery issued by IOC Northern region New Delhi |  | 0 | [18 empty] | 0 | [6 empty] | 0 |  |  |  |  | 0 | 0 |  | 0 | [5 empty] | 0 |  |  | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 478.9 | 478.9 | 482.3 | 451.1 | 452.2 | 452.2 | 452.2 | 452.2 | 481.4 | 481.4 | 481.4 | 481.4 | 481.4 | 481.4
| g) | All india average consuer prize index for industrial worker(base 1982=100)as published by labour bureau ,Govt of india and circulated by emo. | Index No | 111.9552 | [18 empty] | 117.3648 |  |  |  |  | 0 | 0 | 118.5408 | 0 |  | 0 | 121.5984 | 122.7744 | 123.0096 |  | 123.7152 | 0 | 123.7152 | 0 | 0 | 0 | 123.9504 | 0 | 0 | 127.008 | 127.4784 | 0 | 0 | 0 | 130.0656 | 129.1248 | 129.5952 | 130.7712 | 130.7712 | 130.7712 | 131.712 | 133.8288 | 135.0048 | 135.0048 | 136.1808 | 138.2976 | 138.3 | 138.3 | 138.3 | 139.3889 | 138.3 | 139.3889 | 132.0093 | 133.0094 | 133.0094 | 144.8832 | 144.8338 | 145.9228 | 145.9228 | 145.9228 | 138.0097 | 147 | 149.1897 | 150.2787 | 151.3677 | 152.4566 | 147.2479 | 149.3073 | 150.337 | 150.337 | 147.0093 | 148 | 148 | 150.64 | 151 | 153 | 160 | 162 | 163 | 165 | 168 | 168
| h) | Index No.of whole sell price in india for iron and steel as published by reserve bank of india bulletein | Index No | 258.3 | [18 empty] | 258.3 | [6 empty] | 258.3 |  |  |  |  | 191 | 258.3 |  | 258.3 | [5 empty] | 258.3 |  |  | 186.9 |  |  |  |  | 169.9 | 256.9 | 233.4 | 191 | 226.2 | 243.3 | 243.9 | 243.4 | 250.8 | 253.5 | 254.9 | 258.9 | 259.3 | 259.2 | 259.9 | 260.1 | 261.2 | 266.2 | 267.2 | 268.7 | 268.3 | 217.22 | 276.7 | 277.3 | 277.9 | 280.13 | 280.6 | 280.6 | 287.4 | 357.1 | 354.6 | 357.9 | 342.5 | 337.9 | 335.2 | 346.1 | 330.6 | 322.7 | 319.1 | 286.1 | 289 | 286 | 286.2 | 286.7 | 286.4 | 296.4 | 288.1 | 291.4 | 291.3
| i) | Index No.of whole sell price in india for non metalic mineral products(Structural Clay Product) as published by RBI. | Index No | 191 | [18 empty] | 191 | [6 empty] | 191 |  |  |  |  | 213 | 191 |  | 191 | [5 empty] | 191.1 |  |  | 190.4 |  |  |  |  | 186.2 | 188.88 | 190.6 | 191.2 | 190.6 | 190.6 | 190.6 | 190.6 | 190.6 | 190.6 | 190.6 | 190.6 | 190.6 | 190.6 | 190.6 | 190.6 | 190.6 | 190.6 | 190.6 | 190.6 | 190.6 | 211.7 | 211.7 | 213.5 | 214.3 | 216.8 | 219.4 | 219.4 | 219.4 | 219.4 | 220.16 | 220.24 | 220.78 | 220.86 | 223.1 | 223.1 | 223.1 | 224 | 224 | 224 | 227.2 | 227.2 | 227.2 | 227.2 | 227.2 | 227.2 | 227.2 | 227.2
| j) | Cement | Index No | 163.8 | [18 empty] | 163.8 | [6 empty] | 163.8 |  |  |  |  | 163.8 | 163.8 |  | 163.8 | [5 empty] | 163.8 |  |  | 162.2 |  |  |  |  | 191.2 | 191.2 | 191.2 | 191.2 | 191.2 | 191.2 | 191.2 | 191.2 | 191.2 | 191.2 | 220.2 | 220.2 | 220.2 | 220.2 | 220.2 | 220.2 | 220.2 | 220.2 | 220.2 | 220.2 | 220.2 | 220.2 | 220.2 | 220.3 | 220.5 | 220.6 | 220.8 | 220.8 | 220.8 | 220.8 | 220.8 | 220.8 | 220.8 | 220.8 | 220.8 | 221.4 | 221.4 | 222.7 | 224.5 | 227.7 | 228.1 | 228.6 | 230.9 | 230.5 | 228.1 | 227.2 | 225.8 | 213.1
| k) | Diesel | Index No | 372 | [18 empty] | 395 | [6 empty] | 372 |  |  |  |  | 396.5 | 400 |  | 400 | [5 empty] | 372 |  |  | 400 |  |  |  |  | 418 | 418 | 418 | 418 | 418 | 418 | 418 | 418 | 418 | 418 | 418 | 418 | 418 | 418 | 418 | 418 | 449.5 | 449.5 | 449.5 | 449.5 | 449.5 | 449.5 | 449.5 | 451.5 | 451.5 | 451.5 | 465.8 | 465.8 | 465.8 | 465.8 | 465.8 | 478.9 | 478.9 | 478.9 | 478.9 | 478.9 | 482.3 | 451.1 | 452.2 | 452.2 | 452.2 | 452.2 | 481.4 | 481.4 | 481.4 | 481.4 | 481.4 | 481.4
|  | Labour Correction Factor |  | 0.2352
Month and Year of Escalation
| Month and Year of Escalation |  | 2009-12-01
| S.No. | Particulars | Units | Rates/Index
| 1 | Power Transformer
| a) | Copper | INR/ MT | 326293
| b) | Electrical Steel sheet -CRGO | INR/ MT | 157341
| c) | Iron & Steel | Index No | 291.4
| d) | Insulating Material | INR/ Kg | 403.35
| e) | Transformer Oil | INR/ KL | 49625
| f) | Labour | Index No. | 168
| 2 | LT Transformer
| a) | Copper | INR/ MT | 326293
| b) | Electrical Steel sheet -CRGO | INR/ MT | 157341
| c) | Iron & Steel | Index No | 291.4
| d) | Insulating Material | INR/ Kg | 403.35
| e) | Transformer Oil | INR/ KL | 49625
| f) | Labour | Index No. | 168
| 3 | Circuit Breaker
| a) | Iron & Steel | Index No. | 291.4
| b) | Copper | INR/ MT | 326293
| c) | Alluminium | INR/ MT | 151150
| d) | Epoxy Resin | INR/ Kg | 188
| e) | Labour | Index No. | 168
| 4 | Current Transformer and Voltage Transformer
| a) | Index No.for Insulator | Index No | 158.03
| b) | Iron & Steel | Index No | 291.4
| c) | Transformer Oil | INR/ KL | 49625
| d) | Index No.for Insulator | Index No | 158.03
| e) | Electrical Steel sheet -CRGO | INR/ MT | 157341
| f) | Copper | INR/ MT | 326293
| g) | Alluminium | INR/ MT | 151150
| h) | Epoxy Resin | INR/ Kg | 188
| i) | Labour | Index No | 168
| 5 | Isolator
| a) | Iron & Steel | Index No | 291.4
| b) | Copper | INR/ MT | 326293
| c) | Alluminium | INR/ MT | 151150
| d) | Epoxy Resin | INR/ Kg | 188
| e) | Labour | Index No. | 168
| 6 | Surge Arrester
| a) | Zinc | INR/ MT | 123700
| b) | Cobalt | INR/ Kg | 2336.41
| c) | Alluminium | INR/ MT | 151150
| d) | Ball clay | INR/ MT | 2275
| e) | Bismath | INR/ Kg | 951.89
| f) | Fuels/power | Index No | 344.6
| g) | Labour | Index No | 168
| 7 | Substation Structures including bolts and Nuts
| a) | Published Price Index of Structurel Steel | Index No | 48047
| b) | Published Price Index of Electrolytic Zinc | INR / MT | 123700
| c) | Labour | Index No | 168
| 8 | Index No of INSLR |  | 158.03
| a) | Transformer Oil | INR/ KL | 49625
| b) | Labour | Index No | 168
| 9 | PVC/XLPE Insulated Power and Control Cables
| a) | PVC Compound | INR / MT | 90500
| b) | Metal | INR / MT | 127200
| c) | Alliminium | INR / MT | 124933
| d) | Copper | INR / MT | 361737
| e) | Weight in MT of metal KM (Size wise) |  | 0
| f) | IOC _HST basic ceiling selling price ex -refinery issued by IOC Northen region New Delhi |  | 481.4
| g) | All india average consuer prize index for industrial worker(base 1982=100)as published by labour bureau, Govt of india and circulated by emo. | Index No | 168
| h) | Index No.of whole sell price in india for iron and steel as published by reserve bank of india bulltein | Index No | 291.4
| i) | Index No.of whole sell price in india for non metalic mineral products(Structurel clay product) as published by RBI. | Index No | 227.2
| j) | Cement | Index No | 213.1
| k) | Diesel | Index No | 481.4
|  | Labour Correction Factor |  | 0.2352
Note on C78: Base of Labour Index was changed in 2005. Hence, a labour correction factor has been applied to reflect true escalation in labou cost

## Database
CERC
Capital Cost Benchmarking
Project Costs (Actual)
|  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65
|  | Name of the Utility |  | PGCIL | PGCIL | PGCIL | PGCIL | PGCIL | PGCIL | PGCIL | PGCIL | PGCIL | PGCIL | PGCIL | PGCIL | PGCIL | PGCIL | PGCIL | PGCIL | PGCIL | PGCIL | PGCIL | PGCIL | RVPN | APTRANSCO | MSETCL | MSETCL | MSETCL | NSPCL -Sail power company for Bilai steel plant | PGCIL | PGCIL | PGCIL | PGCIL | PGCIL | PGCIL | PGCIL | PGCIL | PGCIL | PGCIL | PGCIL | PGCIL | PGCIL | PGCIL | PGCIL | PGCIL | PGCIL | PGCIL | PGCIL | PGCIL | PGCIL | PGCIL | PGCIL | PGCIL | PGCIL | PGCIL | PGCIL | PGCIL | PGCIL | PGCIL | PGCIL | PGCIL | PGCIL | PGCIL | PGCIL | PGCIL | PGCIL | PGCIL | PGCIL
|  | Name of sub-station |  | 400/220 kV S/S, ARASUR(New) | 400/220 kV S/S AT,ROORKEE | 400/220 kV S/S, PUGALUR(New) | 400/220 kV S/S, DAMOH (New) | 400/220 kV S/S, KARAIKUDI(New) | 400/220 kV S/S AT, WARANGAL | Kankroli | Kaithal | Tirunelveli | Shubashgram | Raigarh | Amritsar | Kolar,Munirabad & Somanahalli extn works | Ludhiyana, Extn of Jalandhar & Malerakotla | Fatehabad | Gwalior | Patna | Muzaffarpur & Biharsheriff | Narendra | Melakottaiyur | Jaisalmer -Rajasthan State | Malkaram - A.P.TRANSCO | Koradi- Maharastra | Khaparkheda - MSETCL- Maharastra | Chakan- MSETCL- Maharastra | NSPCL -Sail power company for Bilai steel plant | Shulajpur(New), Dehgam & VAPI (Extn Works) | Mandola,MalerakotlaBiharsherief, Hyderabad & Durgapaur | (Extn Works), GWALIOR, WARDHA, PUNE, RAIPUR | Pirana,Gwaliar & Bina | GIS New Delhi | Gwalior | Batapara | Amritsar | Navi Mumbai | Kota | Kankroli | Ludhiyana | Fathebad | Moga | Sonepat | Khandwa | Dehgan | 765 kV & 400 kV pooling station- Bihar sherief (Balia,Phathepur, Agra, Lucknow) | Ludhiyana | Trivandrum, & Madurai | Udamalpet & Trichi | Fathebad | Patna | Ranchi | Bihar Sharif | Shujalpur | Kankroli | Kota | Bihar Sharif,Sasaram & Ranchi | Gaya, DVC & Maithon | Lucknow | Agra | Fatepur | Balia | Allahabad | Itarsi | Vijayawada | Rourkela | Tiruvanneli
|  | Reference P.O. No. |  | Ref:- LOA-55803-S119A-7/LOA-1/1986 &1987 Dated 10-03-2006 | Ref-C-13901-S919A-3/LOA-I/2198 & 2199 DATED 01/11/2006 | Ref:- LOA C-55802-S119A-7/LOA-1/1966 &1967(Proj-1) Dated 24/02/06 | Ref:- LOA C-56204-S919A-3/LOA-I/2025 & 2026 DATED:20/04/06 | Ref:- LOA C-56301-S919A-3/LOA-II/2128&2129 dated 23-08-2006 | Ref-C-55807-S119A-7/LOA-I-2020 & 2021 DATED 31/03/2006 | C-13502-S919A-3/LOA-I/1905 & 2021 DT: 16/01/2006 | C-1128-S948-3/LOA-I/1064 DT: 28/03/2003 | C-52705-S919A-3/LOA-II/1842 DT: 02/11/2005 | C-42406-S919A-3/LOA-I/1237 & 1238 DT: 30/01/2004 | C-32306-S919A-3/LOA-I/1424 DT: 11/10/2004 | C-21501-S919A-3/LOA-I/1349 & 1350 | LTCD/EIC/PGCIL/56004/ONLN /2005/101 | C-21702-S919A-3/LOA-I/1759 | C-21703-S919A-3/LOA-I/1718 | .C-324054-S919-3/LOA-I/1549 DT: 14-03-05 | :C-45907-S919A-3/L0A-I/1708 | C-42407-S919A-3/LOA-I/1294 DT: 29/03/2004 | C-55102-S919A-3/LOA-1/1208 dt: 31/12/2003: | C-56103-S919A-3/LOA-I/1921 dated 31/01/2006 | RVPN:400 kV Design/Xtn(Tr)/TN-231/Supply/PO274/D.1236. Jaipur Dt:22-04-08 | OM - 0332 CE/Const./400KV/SE.PM-II/D2-A1/MLKM/Supply/D. No. 604/2008 Dated - 20/09/2008 - Supply of Equipments and Material | REF: TBMS/08/E1036/PD Rev 01 DT 12.5.09 | REF: No.MSETCL/CO/Tr. Proj./TKP/2007-08/23 DT: 30-11-07 | REF: No.MSETCL/CO/Tr. Proj./TKP/2007-08/23 DT: 30-11-07 | LOA No.C&M-101-231-080-9-FC-NOA-6 dated 15.12.2005 | 55701-S116-3/LOA-1/2582 &2583 Dated 14-07-2008 | C-00703 -S-916-3/LOA-1/2340: DT:18-04-2007 | 33501-S116-3/LOA-I/2534 DT: 02-05-2008 : | C-33501-S116-3/LOA-1/2534 & 2535 Dt:02-05-2008 | C-41414-S919 A-I/1553 DT:29-03-2005 : | C-32404-S116-3I/1LOA/1582 DT: 24-03-2005 : | C-32404-S116-3I/1LOA/1582 DT: 24-03-2005 : | C-22101-S916-3/LOA/1980 DT: 02-03-2006 | C-33402-S119A-3/LOA-II/2472 DT:20/03/2008: | C-13501-S917-3/LOA/1730 | C-13501-S917-3/LOA/1730 | C-21702-S916-3/LOA/1535 DT: 07-03-2005 : | C-21702-S916-3/LOA/1535 DT: 07-03-2005 : | C-22101-S916-3/LOA/1980 DT: 02-03-2006 : | C-14404-S-116-3/C-156/LOA-12462 DT;20-03-08 | C-33601-S117-7/LOA-I/2458 & LOA -II / 2459 DT:05-03-2008 : | C-33601-S117-7/LOA-I/2458 & LOA -II / 2459 DT:05-03-2008 : | C-14803-S117-3/LOA-1/2708: DT:22-10-2008 : | C-21702-S917-3/LOA/1664 DT: 04-05-2005 : | C -56401 - S117 - 3 / LOA - 1 / 2478 DT: 25 - 03 - 2008 : | C -56401 - S117 - 3 / LOA - 1 / 2478 DT: 25 - 03 - 2008 : | C-21702-S917-3/LOA/1664 DT: 04-05-2005 | C-45906-S917-3/LOA/1438 DT: 20-10-2004 : | C-45906-S917-3/LOA/1438 DT: 20-10-2004 | C-45906-S917-3/LOA/1438 DT: 20-10-2004 : | C -33701 - S117 - 3 / P-165/LOA-1/2584 & 2585 DT: 14 - 07 - 2008 : | C-13501-S917-3/LOA/1730 Dt:18-10-04 | C-13501-S917-3/LOA/1730 Dt:18-10-04 | C -47208 - S117 - 3 / LOA - 1 / 2706 DT: 22 -10 - 2008 | C -47208 - S117 - 3 / LOA - 1 / 2706 DT: 22 -10 - 2008 | C -47208 - S117 - 3 / LOA - 1 / 2706 DT: 22 -10 - 2008 | C -47208 - S117 - 3 / LOA - 1 / 2706 DT: 22 -10 - 2008 | C -14803 - S117 - 3 / LOA - 1 / 2708 & 2709 DT:22 - 10 - 2008 : | C -14803 - S117 - 3 / LOA - 1 / 2708 & 2709 DT:22 - 10 - 2008 : | C -00704 - S917 - 3 / LOA - 1 / 2365 & 2366 DT: 25 - 06 - 2007 | C -00704 - S917 - 3 / LOA - 1 / 2365 & 2366 DT: 25 - 06 - 2007 | C -00704 - S917 - 3 / LOA - 1 / 2365 & 2366 DT: 25 - 06 - 2007 | C -00704 - S917 - 3 / LOA - 1 / 2365 & 2366 DT: 25 - 06 - 2007 | C-45906-S917-3/L0A/1438 DT:13-06-2005:
|  | Base Data of Indices |  | 2005-08-01 | 2006-04-01 | 2005-08-01 | 2006-01-01 | 2006-04-01 | 2005-08-01 | 2005-05-01 | 2002-06-01 | 2005-05-01 | 2003-08-01 | 2004-03-01 | 2003-08-01 | 2004-11-01 | 2004-09-01 | 2004-09-01 | 2004-09-01 | 2004-08-01 | 2003-09-01 | 2003-08-01 | 2005-05-01 | 2007-10-01 | 2008-03-01 | 2009-01-01 | 2007-10-01 | 2007-10-01 | 2005-08-01 | 2007-12-01 | 2006-12-01 | 2007-07-01 | 2007-07-01 | 2004-08-01 | 2004-08-01 | 2004-08-01 | 2005-09-01 | 2007-11-01 | 2004-09-01 | 2004-09-01 | 2004-07-01 | 2004-07-01 | 2005-09-01 | 2007-09-01 | 2007-08-01 | 2007-08-01 | 2007-08-01 | 2004-07-01 | 2007-09-01 | 2007-09-01 | 2004-07-01 | 2004-03-01 | 2004-03-01 | 2004-03-01 | 2007-12-01 | 2005-01-01 | 2004-09-01 | 2008-04-01 | 2008-04-01 | 2008-04-01 | 2008-04-01 | 2008-04-01 | 2008-04-01 | 2006-12-01 | 2006-12-01 | 2006-12-01 | 2006-12-01 | 2005-05-01
| S.No. | Name of the Component | Unit
| 1 | Power Transformer
| a) | ICT 400/√3/220 √3/ 33KV,167 MVA, single phase autotransformer including Insulating Oil Frieght & Insurance | INR Lakhs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414.69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) | I.C.T 315 MVA, 3 Phase, 400/220/33 KV including including Insulating Oil Frieght & Insurance | INR Lakhs | 617.26 | 0 | 699.67 | 0 | 0 | 723.28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 790.61 | 0 | 0 | 0 | 691.81 | 800.8333 | 896 | 837.75 | 870 | 533.3172 | 530.36 | 534.69 | 708.39 | 1023.72 | 522.4 | 522.97 | 544.81 | 544.81 | 0 | 841.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| c) | ICT 400/√3/220 √3/ 33KV,105 MVA, single phase autotransformer including Insulating Oil Frieght & Insurance | INR Lakhs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 392.75 | 391.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| d) | I.C.T 250 MVA, 3 Phase, 400/220/33 KV including including Insulating Oil Frieght & Insurance |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 642.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | Shunt Reactor
| a) | 420KV, 125 MVAR, 3-Phase Shunt Reactor | INR Lakhs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 408 | 412 | 323.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 409.35 | 408.5 | 405.3 | 404.15 | 404.15 | 408.15 | 0 | 0 | 0 | 0 | 0
| b) | 420KV, 80 MVAR, 3-Phase Shunt Reactor | INR Lakhs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 228 | 217.25 | 228 | 237.25 | 0 | 0 | 256.3 | 0 | 0 | 0 | 0 | 347.65 | 0 | 0 | 0 | 0 | 0 | 0
| c) | 420KV, 63/50 MVAR, 3-Phase Shunt Reactor | INR Lakhs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 258 | 354.5 | 350.9 | 217 | 205 | 0 | 0 | 333.9 | 234.5 | 0 | 320.9 | 322.25 | 0 | 319.05 | 0 | 0 | 312.5 | 307 | 312 | 316 | 274.85
| d) | NGR with oil, for above 400 kV Shunt Reactor | INR Lakhs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.7167 | 0 | 0 | 0 | 0 | 16.6 | 0 | 0 | 23.3 | 17.6 | 0 | 23.6 | 23.65 | 0 | 23.45 | 23.45 | 0 | 0 | 0 | 0 | 0 | 16.75
| e) | Surge Arrestors 120 kV for NGR | INR Lakhs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0 | 0 | 0 | 0 | 1.3 | 0 | 0 | 0.95 | 1.6 | 0 | 0.95 | 0.95 | 0 | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 2.25
| f) | Spares for NGR &120KV SA | INR Lakhs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | Bus Reactor
| a) | 125 MVAR 400 kV | INR Lakhs
| b) | 80 MVAR 400 kV | INR Lakhs
| c) | 63 / 50 MVAR 400 kV | INR Lakhs
| d) | 50 MVAR | INR Lakhs
| e) | Oil for shunt Reactor | INR Lakhs
| f) | Spares for Bus Reactor | INR Lakhs
| 4 | 420 kV Equipments
| a) | 420 kV Breakers with CR | INR Lakhs | 1: 0; 2: 0; 3: 0; 4: 34.834; 5: 0; 6: 0; 7: 40.17; 8: 0; 9: 31.3629; 10: 29.4436; 11: 30.6716; 12: 0; 13: 0; 14: 0; 15: 0; 16: 38.66; 17: 39.8675; 18: 0; 19: 0; 20: 0; 21: 0; 22: 0; 23: 0; 24: 38.21; 25: 35.76; 26: 37.51; 27: 0
| b) | 420 kVBreakers without CR | INR Lakhs | 1: 32.7047; 2: 37.11; 3: 30.5214; 4: 27.4449; 5: 27.0111; 6: 31.1231; 7: 46.08; 8: 29.7294; 9: 27.9334; 10: 27.413; 11: 28.1005; 12: 29.29; 13: 33.55; 14: 33.91; 15: 26.7624; 16: 32.76; 17: 29.1339; 18: 43.36; 19: 24.711; 20: 39.67; 21: 26.61; 22: 32.91; 23: 24.77; 24: 38.21; 25: 35.76; 26: 33.93; 27: 0
| c) | 420 kV CTs 2000A, 40KA, 5-Core, | INR Lakhs | 1: 5.3633; 2: 7.85; 3: 4.64; 4: 5.1723; 5: 5.0906; 6: 7.1184; 7: 7.22; 8: 3.2655; 9: 5.1442; 10: 5.0814; 11: 4.7705; 12: 5.5; 13: 5.85; 14: 6.05; 15: 4.7349; 16: 5.84; 17: 5.7593; 18: 5.04; 19: 4.5531; 20: 6.96; 21: 5.15; 22: 7.14; 23: 5.46; 24: 7.26; 25: 6.8; 26: 6.34; 27: 0
| d) | 420 kv CVT 4400 PF | INR Lakhs | 1: 3.1231; 2: 6.01; 3: 3.01; 4: 3.1139; 5: 3.2206; 6: 4.8407; 7: 5.21; 8: 2.3003; 9: 4.3113; 10: 4.0651; 11: 3.8194; 12: 4.25; 13: 0; 14: 5.03; 15: 2.8821; 16: 4.8728; 17: 3.741; 18: 5.81; 19: 2.794; 20: 5.05; 21: 3.6; 22: 4.39; 23: 3.26; 24: 4.65; 25: 4.35; 26: 5.07; 27: 0
| e) | 420 kv CVT 8800 PF | INR Lakhs | 1: 0; 2: 0; 3: 0; 4: 0; 5: 0; 6: 0; 7: 0; 8: 0; 9: 0; 10: 0; 11: 0; 12: 0; 13: 0; 14: 0; 15: 0; 16: 4.9908; 17: 0; 18: 0; 19: 0; 20: 0; 21: 0; 22: 0; 23: 0; 24: 0; 25: 0; 26: 0; 27: 0
| f) | 420 KV,2000 A,40 kA Isolators 3-Phase with one E/S (3 Phase) with insulators | INR Lakhs | 1: 5.93; 2: 5.58; 3: 6.2; 4: 8.15; 5: 4.91; 6: 5.75; 7: 7.99; 8: 5.91; 9: 6.59; 10: 7.51; 11: 7.17; 12: 9.2; 13: 6.1; 14: 7.73; 15: 8.67; 16: 7.46; 17: 8.36; 18: 9.01; 19: 8.75; 20: 8.82; 21: 8.59; 22: 6.7; 23: 4.59; 24: 4.08; 25: 0; 26: 4.07; 27: 0
| g) | 420 KV,2000A,40 kA Isolators 3-Phase with two E/S with insulators | INR Lakhs | 1: 6.86; 2: 6.78; 3: 7.15; 4: 9.35; 5: 7.51; 6: 6.83; 7: 9.45; 8: 7.01; 9: 7.72; 10: 8.76; 11: 8.27; 12: 10.15; 13: 0; 14: 9.03; 15: 10.11; 16: 8.68; 17: 9.55; 18: 0; 19: 10.02; 20: 10.22; 21: 9.67; 22: 7.92; 23: 5.28; 24: 5.03; 25: 0; 26: 4.64; 27: 0
| h) | 420 KV,2000A,40 kA Isolators one Phase with one E/S | INR Lakhs | 1: 0; 2: 0; 3: 0; 4: 0; 5: 0; 6: 0; 7: 0; 8: 0; 9: 0; 10: 0; 11: 0; 12: 0; 13: 2.03; 14: 0; 15: 0; 16: 0; 17: 0; 18: 0; 19: 0; 20: 0; 21: 0; 22: 0; 23: 1.53; 24: 2.05; 25: 0; 26: 0; 27: 0
| j) | Surge Arrestors 390 kV | INR Lakhs | 1: 0.88; 2: 1.1; 3: 1.65; 4: 1.48; 5: 0.98; 6: 0.99; 7: 1.44; 8: 1.47; 9: 1.3228; 10: 1.4962; 11: 1.303; 12: 1.3; 13: 1.36; 14: 1.51; 15: 1.48; 16: 1.46; 17: 1.67; 18: 2.7; 19: 1.78; 20: 1.39; 21: 1.02; 22: 1.3; 23: 1.01; 24: 1.49; 25: 1.39; 26: 0.99; 27: 0
| 5 | 400 kV Control and Protection Panel
| a) | Circuit Breaker panel with Auto Reclose | INR Lakhs | 1: 7.59; 2: 0; 3: 6.4634; 4: 6.44; 5: 5.3593; 6: 9.7854; 7: 10.84; 8: 1.4413; 9: 10.4546; 10: 2.59; 11: 3.5035; 12: 2.219; 13: 0; 14: 21.48; 15: 8.291; 16: 20.7796; 17: 4.2578; 18: 0; 19: 2.6706; 20: 11.1874; 21: 13.71; 22: 6.7; 23: 10.54; 24: 0; 25: 0; 26: 0; 27: 0
| b) | Circuit Breaker panel without Auto Reclose | INR Lakhs | 1: 6.28; 2: 0; 3: 5.2334; 4: 6.44; 5: 5.6121; 6: 8.172; 7: 9.04; 8: 1.1316; 9: 9.7268; 10: 5.26; 11: 1.9371; 12: 1.5022; 13: 0; 14: 15.82; 15: 8.138; 16: 15.2946; 17: 3.2234; 18: 0; 19: 1.9373; 20: 9.6366; 21: 0; 22: 4.54; 23: 0; 24: 0; 25: 0; 26: 0; 27: 0
| c) | Line protection panel | INR Lakhs | 1: 35.67; 2: 0; 3: 27.2149; 4: 13.58; 5: 13.2971; 6: 18.2784; 7: 15.03; 8: 10.602; 9: 17.988; 10: 16.9; 11: 15.6788; 12: 23.5417; 13: 0; 14: 24.54; 15: 20.3833; 16: 23.6787; 17: 30.3171; 18: 0; 19: 16.3716; 20: 18.7508; 21: 16.0707; 22: 14.74; 23: 22.18; 24: 20.36; 25: 16.94; 26: 0; 27: 0
| d) | Transformer protection panel(both HV and MV) | INR Lakhs | 1: 19.71; 2: 0; 3: 17.0115; 4: 18.76; 5: 17.1901; 6: 11.6122; 7: 12.83; 8: 5.2082; 9: 27.6636; 10: 9.8; 11: 8.5587; 12: 6.0186; 13: 0; 14: 19.82; 15: 20.7765; 16: 19.1139; 17: 19.1711; 18: 0; 19: 9.3782; 20: 11.7769; 21: 16.39; 22: 17.87; 23: 25.19; 24: 26.1; 25: 0; 26: 0; 27: 0
| e) | Reactor protection panel | INR Lakhs | 1: 0; 2: 0; 3: 0; 4: 13.63; 5: 12.5387; 6: 0; 7: 13.12; 8: 0; 9: 13.6729; 10: 0; 11: 6.4227; 12: 0; 13: 0; 14: 14.82; 15: 13.4468; 16: 14.3748; 17: 13.5178; 18: 0; 19: 0; 20: 8.5858; 21: 11.1; 22: 0; 23: 0; 24: 0; 25: 0; 26: 0; 27: 0
| f) | Bus Bar Protection Panel | INR Lakhs | 1: 107.73; 2: 0; 3: 181.7768; 4: 159.75; 5: 96.366; 6: 68.2813; 7: 133.64; 8: 5.16; 9: 210.46; 10: 29.66; 11: 89.02; 12: 16.94; 13: 0; 14: 244.09; 15: 107.4546; 16: 234.94; 17: 181.9648; 18: 0; 19: 6.1789; 20: 123.2905; 21: 109.3; 22: 44.16; 23: 133.58; 24: 37.9; 25: 35.69; 26: 0; 27: 0
| 6 | 245 kV Equipment
| a) | Circuit Breakers 245 kV
|  | 1600 A, 40 kA | INR Lakhs | 1: 12.02; 2: 15.97; 3: 14.489; 4: 13.1947; 5: 12.9861; 6: 12.7388; 7: 12.46; 8: 10.92; 9: 12.0753; 10: 12.0232; 11: 12.1873; 12: 12.1; 13: 14.21; 14: 14.72; 15: 12.3519; 16: 14.3145; 17: 12.6247; 18: 0; 19: 11.7864; 20: 16.49; 21: 11.61; 22: 13.98; 23: 11.24; 24: 16.05; 25: 15.02; 26: 14.04; 27: 0
|  | 2500 A, 40 kA | INR Lakhs | 1: 12.02; 2: 16.8; 3: 14.489; 4: 13.1947; 5: 12.9861; 6: 12.7388; 7: 12.46; 8: 10.92; 9: 12.0753; 10: 12.7583; 11: 12.2425; 12: 12.1; 13: 14.21; 14: 14.72; 15: 12.3519; 16: 14.3145; 17: 12.6247; 18: 0; 19: 11.7864; 20: 16.49; 21: 0; 22: 13.98; 23: 0; 24: 0; 25: 0; 26: 14.05; 27: 0
| b) | Current Transformers 245 kV |  | 4: 0; 5: 0; 6: 0; 8: 0; 9: 0; 10: 0; 11: 0; 12: 0; 13: 0; 14: 0; 15: 0; 16: 0; 17: 0; 18: 0; 19: 0; 20: 0; 21: 0; 22: 0; 23: 0; 24: 0; 25: 0; 26: 0; 27: 0
|  | 1600 A, 40 kA , 5 core, with 120% extended current | INR Lakhs | 1: 2.7255; 2: 3.34; 3: 2.3; 4: 2.6389; 5: 2.5972; 6: 3.4449; 7: 3.79; 8: 1.8119; 9: 2.4986; 10: 2.3374; 11: 2.3642; 12: 2.05; 13: 2.96; 14: 2.84; 15: 2.3674; 16: 2.7449; 17: 2.8313; 18: 0; 19: 2.0489; 20: 3.5704; 21: 0; 22: 3.69; 23: 3.4817; 24: 0; 25: 0; 26: 0; 27: 0
|  | 1600 A, 40 kA, 5 core, with 150% extended current | INR Lakhs | 1: 2.8369; 2: 3.34; 3: 2.43; 4: 2.6917; 5: 2.6492; 6: 3.5061; 7: 3.85; 8: 1.9095; 9: 2.4986; 10: 2.4391; 11: 2.3958; 12: 2.07; 13: 0; 14: 2.84; 15: 2.4395; 16: 2.7449; 17: 2.9886; 18: 0; 19: 2.47; 20: 3.6283; 21: 0; 22: 0; 23: 3.9202; 24: 4.14; 25: 3.87; 26: 4.53; 27: 0
| c) | Capacitive Voltage Transformer 245 kV |  | 4: 0; 5: 0; 6: 0; 8: 0; 9: 0; 10: 0; 11: 0; 12: 0; 13: 0; 14: 0; 15: 0; 16: 0; 17: 0; 18: 0; 19: 0; 20: 0; 21: 0; 22: 0; 23: 0; 24: 0; 25: 0; 26: 0; 27: 0
|  | 8800 pf, S- Ph, with 3 secondaries | INR Lakhs | 1: 0; 2: 0; 3: 0; 4: 0; 5: 0; 6: 0; 7: 0; 8: 0; 9: 0; 10: 0; 11: 0; 12: 0; 13: 0; 14: 0; 15: 0; 16: 0; 17: 0; 18: 0; 19: 0; 20: 0; 21: 0; 22: 0; 23: 0; 24: 0; 25: 0; 26: 0; 27: 0
|  | 4400 pf, S- Ph with 3 secondaries | INR Lakhs | 1: 2.3813; 2: 3.56; 3: 2.09; 4: 2.2167; 5: 2.1817; 6: 2.5314; 7: 2.81; 8: 1.7928; 9: 2.4986; 10: 2.4391; 11: 2.2255; 12: 2.32; 13: 2.96; 14: 2.65; 15: 1.9042; 16: 2.5499; 17: 2.5772; 18: 0; 19: 1.7385; 20: 2.7575; 21: 2.5; 22: 3.2; 23: 0; 24: 0; 25: 0; 26: 3.4; 27: 0
| d) | Isolators 245 kV |  | 4: 0; 5: 0; 6: 0; 8: 0; 9: 0; 10: 0; 11: 0; 12: 0; 13: 0; 14: 0; 15: 0; 16: 0; 17: 0; 18: 0; 19: 0; 20: 0; 21: 0; 22: 0; 23: 0; 24: 0; 25: 0; 26: 0; 27: 0
|  | 1600A, 40 kA, DB Type with two E/S | INR Lakhs | 1: 2.9; 2: 3.45; 3: 2.85; 4: 3.88; 5: 2.2825; 6: 2.72; 7: 3.72; 8: 2.88; 9: 3.22; 10: 3.42; 11: 3.7; 12: 3.28; 13: 2.89; 14: 3.57; 15: 3.58; 16: 3.46; 17: 3.68; 18: 0; 19: 3.75; 20: 3.88; 21: 4.72; 22: 3.67; 23: 0; 24: 0; 25: 0; 26: 3.09; 27: 0
|  | 1600A, 40 kA, DB Type with one E/S | INR Lakhs | 1: 2.46; 2: 2.91; 3: 2.51; 4: 3.29; 5: 1.6213; 6: 2.33; 7: 3.18; 8: 2.43; 9: 2.8; 10: 2.91; 11: 3.15; 12: 2.82; 13: 2.38; 14: 3.07; 15: 4.3094; 16: 2.97; 17: 3.16; 18: 0; 19: 3.12; 20: 3.36; 21: 3.8; 22: 3.23; 23: 3.2; 24: 1.67; 25: 0; 26: 2.53; 27: 0
|  | 1600A, 40 kA, DB, Tandem Type without E/S | INR Lakhs | 1: 2.07; 2: 2.39; 3: 2.22; 4: 3.79; 5: 2.5186; 6: 1.98; 7: 3.4; 8: 2.01; 9: 2.43; 10: 2.42; 11: 2.6; 12: 2.53; 13: 0; 14: 2.94; 15: 3.03; 16: 2.49; 17: 2.63; 18: 0; 19: 2.58; 20: 2.87; 21: 0; 22: 0; 23: 2.86; 24: 1.14; 25: 0; 26: 2.09; 27: 0
|  | 2500A, 40 KA, DB Type with Two E/S | INR Lakhs | 1: 3.02; 2: 3.63; 3: 2.99; 4: 4.09; 5: 2.0239; 6: 2.81; 7: 3.91; 8: 2.93; 9: 3.38; 10: 3.51; 11: 3.81; 12: 3.77; 13: 0; 14: 3.65; 15: 4.28; 16: 3.54; 17: 3.78; 18: 0; 19: 3.68; 20: 4.06; 21: 0; 22: 0; 23: 0; 24: 0; 25: 0; 26: 3.14; 27: 0
|  | 1600A, 40 kA with one E/S S-phase | INR Lakhs | 1: 0; 2: 0; 3: 0; 4: 0; 5: 0; 6: 0; 7: 0; 8: 0; 9: 0; 10: 0; 11: 0; 12: 0; 13: 1.27; 14: 0; 15: 0; 16: 0; 17: 0; 18: 0; 19: 0; 20: 0; 21: 0; 22: 0; 23: 0; 24: 0; 25: 0; 26: 0; 27: 0
|  | 1600A, 40 kA without E/S S phase | INR Lakhs | 1: 0; 2: 0; 3: 0; 4: 0; 5: 0; 6: 0; 7: 0; 8: 0; 9: 0; 10: 0; 11: 0; 12: 0; 13: 0.86; 14: 0; 15: 0; 16: 0; 17: 0; 18: 0; 19: 0; 20: 0; 21: 0; 22: 0; 23: 0; 24: 0; 25: 0; 26: 0; 27: 0
| e) | 216 kV Surge Arrestors |  | 1: 0.38; 2: 0.53; 3: 0.59; 4: 0.55; 5: 0.62964; 6: 0.52; 7: 0.75; 8: 0.62; 9: 0.59772; 10: 0.5878; 11: 0.6199; 12: 0.45; 13: 0.68641; 14: 0.63; 15: 0.59; 16: 0.61; 17: 0.57; 18: 0; 19: 0.66; 20: 0.72; 21: 0.32; 22: 0.55; 23: 0.38; 24: 0.51; 25: 0.48; 26: 0.37; 27: 0
| f) | 220 kV Control & Potection Panel |  | 4: 0; 5: 0; 6: 0; 7: 0; 8: 0; 9: 0; 10: 0; 11: 0; 12: 0; 13: 0; 14: 0; 15: 0; 16: 0; 17: 0; 18: 0; 19: 0; 20: 0; 21: 0; 22: 0; 23: 0; 24: 0; 25: 0; 26: 0; 27: 0
|  | Circuit Breaker panel with Auto Reclose | INR Lakhs | 1: 6.28; 2: 0; 3: 5.2334; 4: 6.44; 5: 5.6121; 6: 9.7854; 7: 10.8381; 8: 1.4413; 9: 10.4546; 10: 5.2568; 11: 4.2295; 12: 2.219; 13: 0; 14: 21.48; 15: 8.291; 16: 20.7796; 17: 4.1909; 18: 0; 19: 2.6706; 20: 11.1874; 21: 0; 22: 0; 23: 0; 24: 0; 25: 0; 26: 0; 27: 0
|  | Circuit Breaker panel without Auto Reclose | INR Lakhs | 1: 6.28; 2: 0; 3: 5.2334; 4: 6.44; 5: 5.3588; 6: 8.1719; 7: 9.0377; 8: 1.1384; 9: 9.7268; 10: 2.5944; 11: 2.3345; 12: 1.5022; 13: 0; 14: 15.82; 15: 8.138; 16: 15.2946; 17: 3.1565; 18: 0; 19: 1.9373; 20: 9.6366; 21: 0; 22: 4.34; 23: 0; 24: 0; 25: 0; 26: 0; 27: 0
|  | Line protection panel | INR Lakhs | 1: 24.86; 2: 0; 3: 18.523; 4: 13.58; 5: 13.2971; 6: 18.2784; 7: 15.0292; 8: 9.8161; 9: 17.988; 10: 13.3411; 11: 18.442; 12: 23.5417; 13: 0; 14: 24.54; 15: 20.3833; 16: 23.6787; 17: 29.8266; 18: 0; 19: 15.9535; 20: 18.7508; 21: 13.71; 22: 12.97; 23: 17.14; 24: 0; 25: 0; 26: 0; 27: 0
|  | Bus Bar Protection panel | INR Lakhs | 1: 65.7; 2: 0; 3: 111.98; 4: 50.22; 5: 45.5033; 6: 47.844; 7: 61.22; 8: 0; 9: 73.68; 10: 18.46; 11: 55.9975; 12: 16.94; 13: 0; 14: 86.27; 15: 55.5788; 16: 82.9071; 17: 90.6302; 18: 0; 19: 0; 20: 48.51; 21: 71.14; 22: 74.16; 23: 85.51; 24: 0; 25: 0; 26: 0; 27: 0
| 7 | Foundations
| a) | ICT -315 MVA | INR Lakhs | 1: 15
| b) | ICT -S-ph 167 MVA | INR Lakhs | 1: 15
| c) | Reactors | INR Lakhs | 1: 10
| d) | 400 kV equipments |  | 1: 0
|  | 420 KV Circuit breakers | INR Lakhs | 1: 1.25
|  | 420KV Isolators | INR Lakhs | 1: 0.5
|  | 420 KV Current Transformers | INR Lakhs | 1: 0.1
|  | 420KV CVT | INR Lakhs | 1: 0.1
|  | 390KV surge Arrestors | INR Lakhs | 1: 0.05
|  | Towers , Lattice Type | INR Lakhs | 1: 3
|  | Lightning cum Lighting Masts | INR Lakhs | 1: 4
|  | B.P.I. | INR Lakhs | 1: 0.05
|  | Line( Wave) Traps both for 400 & 220 kV | INR Lakhs | 1: 0.5
| e) | 220 kV equipments |  | 1: 0
|  | 245 KV Circuit breakers | INR Lakhs | 1: 0.5
|  | 245 KV Isolators | INR Lakhs | 1: 0.4
|  | 245 KV Current Transformers | INR Lakhs | 1: 0.1
|  | 245 KV CVT | INR Lakhs | 1: 0.1
|  | 216 KV surge Arrestors | INR Lakhs | 1: 0.4
|  | Towers , Lattice Type | INR Lakhs | 1: 2.5
|  | BPI | INR Lakhs | 1: 0.4
| f) | L.T Transformers | INR Lakhs | 1: 0.2
| 8 | Firewalls for Single Phase ICT & Reactors | INR Lakhs | bar: 1
| 9 | Common Equipments
| a) | Control & Relay panel.
|  | Complete Substation automation system for 400/230kV S/S including hardware and software for remote control station alongthwith associated equipments and Kiosks for the following bays ( bays) as defined in the teechnical specification, Sec-Substaion Automation | INR Lakhs | 1: 0; 2: 0; 3: 0; 4: 0; 5: 0; 6: 0; 7: 0; 8: 0; 9: 0; 10: 0; 11: 0; 12: 0; 13: 0; 14: 0; 15: 0; 16: 0; 17: 0; 18: 0; 19: 0; 20: 0; 21: 0; 22: 0; 23: 0; 24: 0; 25: 0; 26: 0; 27: 0
| b) | LT Switchgear |  | 9: 0
|  | 800KVA 33/.400 KV Distribution Transformer | INR Lakhs | 1: 5.28; 2: 18.94; 3: 7.52; 4: 12.21; 5: 13.1704; 6: 10.36; 7: 7.4228; 8: 5.5968; 9: 6.8877; 10: 3.9685; 11: 4.5891; 12: 5.11; 13: 0; 14: 5.27; 15: 6.8085; 16: 5.0728; 17: 4.01; 18: 0; 19: 7.279; 20: 7.279; 21: 13.1221; 22: 7.9671; 23: 0; 24: 0; 25: 0; 26: 5.11; 27: 0
|  | 630KVA, 11/400VKV Distribution Transformer | INR Lakhs | 1: 4.46; 2: 18.11; 3: 5.01; 4: 10.12; 5: 12.7429; 6: 6.21; 7: 5.6954; 8: 3.043; 9: 4.9505; 10: 2.7877; 11: 3.7057; 12: 2.54; 13: 0; 14: 4.4; 15: 4.8985; 16: 4.4548; 17: 3.45; 18: 0; 19: 7.279; 20: 6.3411; 21: 10.44; 22: 6.99; 23: 10.09; 24: 10.09; 25: 0; 26: 2.54; 27: 0
|  | 72.5 kV Isolator with insulators | INR Lakhs | 1: 1.58; 2: 0; 3: 0.74; 4: 0.97; 5: 1.0795; 6: 0.64; 7: 0.85; 8: 0; 9: 0.7; 10: 0.94; 11: 0.61; 12: 0; 13: 0; 14: 0; 15: 0; 16: 0.76; 17: 1.03; 18: 0; 19: 3.616; 20: 3.9776; 21: 2.24; 22: 0.56; 23: 0; 24: 0; 25: 0; 26: 0; 27: 0
|  | 72.5KV , 1250A, 25KA Circuit Breaker | INR Lakhs | 1: 6.14; 2: 0; 3: 6.2786; 4: 5.38; 5: 5.4043; 6: 5.6794; 7: 0; 8: 0; 9: 0; 10: 0; 11: 0; 12: 0; 13: 0; 14: 0; 15: 0; 16: 0; 17: 0; 18: 0; 19: 0.86; 20: 0.82; 21: 0; 22: 0; 23: 0; 24: 0; 25: 0; 26: 0; 27: 0
|  | 72.5KV, 25KA, 3 Core Current Transformer 3 Nos | INR Lakhs | 1: 2.73; 2: 0; 3: 2.52; 4: 2.43; 5: 0.89949; 6: 0.63; 7: 0; 8: 0; 9: 0; 10: 0; 11: 0; 12: 0; 13: 0; 14: 0; 15: 0; 16: 0; 17: 0; 18: 0; 19: 0; 20: 0; 21: 0; 22: 0.84; 23: 0; 24: 0; 25: 0; 26: 0; 27: 0
|  | 72.5KV, 2 Core, 33kV /√3 / 110 V/√3 CVT / PT | INR Lakhs | 1: 2.88; 2: 0; 3: 1.535; 4: 2.43; 5: 0.89949; 6: 0.57; 7: 0; 8: 0; 9: 0; 10: 0; 11: 0; 12: 0; 13: 0; 14: 0; 15: 0; 16: 0; 17: 0; 18: 0; 19: 0; 20: 0; 21: 0; 22: 0.84; 23: 0; 24: 0; 25: 0; 26: 0; 27: 0
|  | Relay panel for 800 kVA Transformer on 72.5 kV side | INR Lakhs | 1: 4.37; 2: 0; 3: 4.06; 4: 6.44; 5: 0; 6: 0; 7: 0; 8: 0; 9: 0; 10: 0; 11: 0; 12: 0; 13: 0; 14: 0; 15: 0; 16: 0; 17: 0; 18: 0; 19: 0; 20: 0; 21: 0; 22: 0; 23: 0; 24: 0; 25: 0; 26: 0; 27: 0
|  | 11KV Horn gap Fuse | INR Lakhs | 1: 0.1; 2: 0; 3: 0.16; 4: 0.13; 5: 0.1799; 6: 0.27; 7: 0.17; 8: 0; 9: 0.21; 10: 0.09; 11: 0.12; 12: 0; 13: 0; 14: 0; 15: 0; 16: 0.12; 17: 0.57; 18: 0; 19: 0; 20: 0; 21: 0; 22: 0.42; 23: 0; 24: 0; 25: 0; 26: 0; 27: 0
|  | 11KV Isolator without ES | INR Lakhs | 1: 0.13; 2: 0; 3: 0.35; 4: 0.54; 5: 0.52469; 6: 0.31; 7: 0; 8: 0; 9: 0.32; 10: 0.57; 11: 0.57; 12: 0; 13: 0; 14: 0; 15: 0; 16: 0.52; 17: 0.56; 18: 0; 19: 0.27; 20: 0.51; 21: 0; 22: 0; 23: 0; 24: 0; 25: 0; 26: 0; 27: 0
|  | 11KV Surge Arrestor. | INR Lakhs | 1: 0.18; 2: 0; 3: 0.07; 4: 0.11; 5: 0.04498; 6: 0.10216; 7: 0; 8: 0; 9: 0.14; 10: 0; 11: 0.15951; 12: 0; 13: 0; 14: 0; 15: 0; 16: 0.39; 17: 0.31; 18: 0; 19: 0.4; 20: 0.39; 21: 0; 22: 0.48; 23: 0.33; 24: 0.33; 25: 0; 26: 0; 27: 0
|  | 415V Main Switch Board | INR Lakhs | 1: 9.4; 2: 13.05; 3: 8.7939; 4: 11.2887; 5: 12.8531; 6: 11.7104; 7: 15.7583; 8: 8.7335; 9: 13.9338; 10: 12.7533; 11: 14.9431; 12: 5.6188; 13: 0; 14: 8.7824; 15: 9.1166; 16: 8.4847; 17: 10.683; 18: 0; 19: 0.12; 20: 0.18; 21: 16.65; 22: 12.09; 23: 0; 24: 0; 25: 0; 26: 5.6188; 27: 0
|  | 415V ACDB | INR Lakhs | 1: 9.75; 2: 6.73; 3: 5.7786; 4: 10.9624; 5: 12.9621; 6: 5.1855; 7: 6.9779; 8: 4.2341; 9: 6.3189; 10: 6.3311; 11: 6.7946; 12: 4.3458; 13: 0; 14: 6.3435; 15: 10.2407; 16: 6.1248; 17: 8.3212; 18: 0; 19: 9.8763; 20: 15.1436; 21: 14.52; 22: 11.48; 23: 13.26; 24: 13.26; 25: 0; 26: 4.3458; 27: 0
|  | 415V MLDB | INR Lakhs | 1: 3.08; 2: 2.93; 3: 2.7317; 4: 2.7593; 5: 4.7462; 6: 3.4583; 7: 4.6537; 8: 1.1055; 9: 3.367; 10: 3.7862; 11: 3.62; 12: 2.107; 13: 0; 14: 2.2738; 15: 3.4602; 16: 2.1959; 17: 3.5488; 18: 0; 19: 6.7868; 20: 6.7057; 21: 4.34; 22: 5.02; 23: 7.56; 24: 7.56; 25: 0; 26: 2.107; 27: 0
|  | 415V Emergency LDB | INR Lakhs | 1: 1.23; 2: 0.79; 3: 1.1557; 4: 0.78811; 5: 0.86147; 6: 1.1776; 7: 1.5847; 8: 0.33676; 9: 0.76104; 10: 1.2509; 11: 0.82; 12: 0.55; 13: 0; 14: 0.50748; 15: 0.62298; 16: 0.48998; 17: 1.2849; 18: 0; 19: 2.697; 20: 4.4722; 21: 1.11; 22: 0; 23: 0.65; 24: 0.65; 25: 0; 26: 0.55; 27: 0
|  | 220V DCDB | INR Lakhs | 1: 2.05; 2: 1.49; 3: 0.9666; 4: 3.1627; 5: 2.2541; 6: 1.2954; 7: 4.3368; 8: 3.0651; 9: 1.3837; 10: 1.4378; 11: 1.484; 12: 1.2291; 13: 0; 14: 1.8883; 15: 3.1753; 16: 1.8419; 17: 1.9579; 18: 0; 19: 0.59511; 20: 1.5229; 21: 3.5865; 22: 2.8; 23: 5.1; 24: 5.1; 25: 0; 26: 1.2291; 27: 0
|  | 50V DCDB | INR Lakhs | 1: 1.52; 2: 1.34; 3: 0.91; 4: 3.1574; 5: 2.1624; 6: 1.0599; 7: 1.7432; 8: 1.8598; 9: 1.2453; 10: 1.3659; 11: 1.3363; 12: 1.1589; 13: 0; 14: 1.5224; 15: 2.8047; 16: 1.4699; 17: 1.86; 18: 0; 19: 2.3551; 20: 1.6752; 21: 3.4511; 22: 3.19; 23: 3.19; 24: 3.19; 25: 0; 26: 1.1589; 27: 0
| b) | 220V Battery | INR Lakhs | 1: 6.39; 2: 6.17; 3: 5.6951; 4: 4.5744; 5: 5.1121; 6: 5.4667; 7: 6.378; 8: 5.2205; 9: 5.5809; 10: 4.5743; 11: 6.3368; 12: 5.22; 13: 0; 14: 6.59; 15: 7.7077; 16: 6.3608; 17: 9.8509; 18: 0; 19: 1.6972; 20: 1.3706; 21: 17.43; 22: 10.41; 23: 7.5021; 24: 7.5021; 25: 0; 26: 5.22; 27: 0
| c) | 50V Battery | INR Lakhs | 1: 1.94; 2: 1.69; 3: 1.414; 4: 1.2147; 5: 1.4523; 6: 1.6566; 7: 1.9327; 8: 1.2157; 9: 1.7588; 10: 1.6634; 11: 1.8731; 12: 1.1913; 13: 0; 14: 1.79; 15: 1.7128; 16: 1.6469; 17: 2.9859; 18: 0; 19: 5.37; 20: 5.4814; 21: 3.8; 22: 7.92; 23: 2.8179; 24: 2.8179; 25: 0; 26: 1.1913; 27: 0
| d) | Battery Charger for 220V Battery | INR Lakhs | 1: 1.5; 2: 2.93; 3: 3.5597; 4: 2.3465; 5: 2.8484; 6: 1.1982; 7: 1.6358; 8: 1.7801; 9: 2.4599; 10: 1.5646; 11: 1.5206; 12: 2.0811; 13: 0; 14: 1.7663; 15: 2.9513; 16: 1.7059; 17: 1.7499; 18: 0; 19: 1.53; 20: 1.625; 21: 3.7; 22: 10.38; 23: 3.6704; 24: 3.6704; 25: 0; 26: 2.0811; 27: 0
| e) | Battery Charger for 50V Battery | INR Lakhs | 1: 1.06; 2: 2.26; 3: 2.6608; 4: 1.7944; 5: 1.835; 6: 1.0955; 7: 1.4956; 8: 1.1337; 9: 1.5887; 10: 1.1043; 11: 1.2886; 12: 1.1775; 13: 0; 14: 1.5224; 15: 1.7439; 16: 1.4699; 17: 1.2971; 18: 0; 19: 2.1457; 20: 1.5177; 21: 1.79; 22: 3.54; 23: 2.8596; 24: 2.8596; 25: 0; 26: 1.1775; 27: 0
| f) | DG Set-250KVA with control panel | INR Lakhs | 1: 13.39; 2: 17.63; 3: 19.62; 4: 22.21; 5: 24.7511; 6: 15.05; 7: 19.35; 8: 10.81; 9: 23.574; 10: 12.09; 11: 13.46; 12: 13; 13: 0; 14: 18.78; 15: 18.7138; 16: 18.3293; 17: 14.68; 18: 0; 19: 1.4955; 20: 1.3154; 21: 17.61; 22: 21.18; 23: 0; 24: 0; 25: 0; 26: 13; 27: 0
| g) | High Wall Type Split AC unit of 2TR Capacity | INR Lakhs | 1: 0.36; 2: 0.44003; 3: 0.3; 4: 0.32; 5: 0.37177; 6: 0.41; 7: 0.49; 8: 0; 9: 0.29232; 10: 0; 11: 0.25; 12: 0.3; 13: 0; 14: 0; 15: 0; 16: 0.48; 17: 0.31; 18: 0; 19: 20.06; 20: 18.62; 21: 0; 22: 0; 23: 0; 24: 0; 25: 0; 26: 0.3; 27: 0
| h) | Illumination(Indoor and Outdoor) | INR Lakhs | 1: 0; 2: 0; 3: 0; 4: 0; 5: 0; 6: 0; 7: 0; 8: 0; 9: 0; 10: 0; 11: 0; 12: 0; 13: 0; 14: 0; 15: 0; 16: 0; 17: 0; 18: 0; 19: 0.38; 20: 0.39; 21: 0; 22: 0; 23: 0; 24: 0; 25: 0; 26: 0; 27: 0
| 10 | PLCC equipments on 400 kV side (Both for 400 & 220 kV) | INR Lakhs | 1: 0; 2: 0; 3: 0; 4: 0; 5: 0; 6: 0; 7: 0; 8: 0; 9: 0; 10: 0; 11: 0; 12: 0; 13: 0; 14: 0; 15: 0; 16: 0; 17: 0; 18: 0; 19: 0; 20: 0; 21: 0; 22: 0; 23: 0; 24: 0; 25: 0; 26: 0; 27: 0
| 11 | Mandatory Spares | INR Lakhs | 1: 0; 2: 0; 3: 0; 4: 0; 5: 0; 6: 0; 7: 0; 8: 0; 9: 0; 10: 0; 11: 0; 12: 0; 13: 0; 14: 0; 15: 0; 16: 0; 17: 0; 18: 0; 19: 0; 20: 0; 21: 0; 22: 0; 23: 0; 24: 0; 25: 0; 26: 0; 27: 0
| 12 | Steel Structures - Unit MT
| a) | Lattice Type | INR Lakhs | 1: 0.6; 2: 0; 3: 0; 4: 0; 5: 0; 6: 0; 7: 0; 8: 0; 9: 0; 10: 0; 11: 0; 12: 0; 13: 0; 14: 0; 15: 0; 16: 0; 17: 0; 18: 0; 19: 0; 20: 0; 21: 0; 22: 0; 23: 0; 24: 0; 25: 0; 26: 0; 27: 0
| b) | Tubular support structures | INR Lakhs | 1: 0.8; 2: 0; 3: 0; 4: 0; 5: 0; 6: 0; 7: 0; 8: 0; 9: 0; 10: 0; 11: 0; 12: 0; 13: 0; 14: 0; 15: 0; 16: 0; 17: 0; 18: 0; 19: 0; 20: 0; 21: 0; 22: 0; 23: 0; 24: 0; 25: 0; 26: 0; 27: 0
| 13 | Earth mat- 40 mm rods - Per kM | INR Lakhs | 1: 6; 2: 0; 3: 0; 4: 0; 5: 0; 6: 0; 7: 0; 8: 0; 9: 0; 10: 0; 11: 0; 12: 0; 13: 0; 14: 0; 15: 0; 16: 0; 17: 0; 18: 0; 19: 0; 20: 0; 21: 0; 22: 0; 23: 0; 24: 0; 25: 0; 26: 0; 27: 0
| 14 | Bus Bar Materials
| a) | 400 kV Switchyard | INR Lakhs | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
A
Moose ACSR
Twin disc Ins. string with Tension Hardware fr Twin Moose
Twin disc Ins. string with Suspension Hardware fr Twin Moose
400KV BPI
Tee Clamp for Twin Moose to 4" IPS Al. Tube
Tee Clamp for Twin Moose to Twin Moose ACSR
PG Clamps
Spacer to Twin Moose ACSR
Ground wire and accessories
| b) | 220 kV Switchyard | INR Lakhs | 1: 180; 2: 0; 3: 0; 4: 0; 5: 0; 6: 0; 7: 0; 8: 0; 9: 0; 10: 0; 11: 0; 12: 0; 13: 0; 14: 0; 15: 0; 16: 0; 17: 0; 18: 0; 19: 0; 20: 0; 21: 0; 22: 0; 23: 0; 24: 0; 25: 0; 26: 0; 27: 0
Quad disc Ins. string with Tension Hardware fr Quad Moose
Twin disc Ins. string with Suspension Hardware fr Quad Moose
Twin disc Ins. string with Tension Hardware fr Twin Moose
Twin disc Ins. string with Suspension Hardware fr Twin Moose
220KV BPI
4" IPS Al. Tube
Moose ACSR
Tee Clamp for Quad Moose to Twin Moose ACSR
Tee Clamp for Twin Moose to Twin Moose ACSR
Tee Clamp for Twin Moose to 4" IPS Al. Tube
Spacer to Quad Moose ACSR
Spacer to Twin Moose ACSR
PG Clamps
Ground wire and accessories
| 15 | Fire fighting Equipment including one 315 MVA Transformer. | INR Lakhs | 1: 75; 2: 0; 3: 0; 4: 0; 5: 0; 6: 0; 7: 0; 8: 0; 9: 0; 10: 0; 11: 0; 12: 0; 13: 0; 14: 0; 15: 0; 16: 0; 17: 0; 18: 0; 19: 0; 20: 0; 21: 0; 22: 0; 23: 0; 24: 0; 25: 0; 26: 0; 27: 0
| 16 | Power Cables -- Cost per kM | INR Lakhs | 1: 1.2; 2: 0; 3: 0; 4: 0; 5: 0; 6: 0; 7: 0; 8: 0; 9: 0; 10: 0; 11: 0; 12: 0; 13: 0; 14: 0; 15: 0; 16: 0; 17: 0; 18: 0; 19: 0; 20: 0; 21: 0; 22: 0; 23: 0; 24: 0; 25: 0; 26: 0; 27: 0
| 17 | Control cables --- Cost per kM | INR Lakhs | 1: 1; 2: 0; 3: 0; 4: 0; 5: 0; 6: 0; 7: 0; 8: 0; 9: 0; 10: 0; 11: 0; 12: 0; 13: 0; 14: 0; 15: 0; 16: 0; 17: 0; 18: 0; 19: 0; 20: 0; 21: 0; 22: 0; 23: 0; 24: 0; 25: 0; 26: 0; 27: 0
| 18 | Land devolopment & Civil engineering works
| a) | Soil Investigation (lump Sum) | INR Lakhs | 1: 2; 2: 0; 3: 0; 4: 0; 5: 0; 6: 0; 7: 0; 8: 0; 9: 0; 10: 0; 11: 0; 12: 0; 13: 0; 14: 0; 15: 0; 16: 0; 17: 0; 18: 0; 19: 0; 20: 0; 21: 0; 22: 0; 23: 0; 24: 0; 25: 0; 26: 0; 27: 0
| b) | Intial Civil Engineering Works like Levelling,Retaining walls, Appoach Road, Peripheral Fencing etc. (lump Sum) | INR Lakhs | 1: 70; 2: 0; 3: 0; 4: 0; 5: 0; 6: 0; 7: 0; 8: 0; 9: 0; 10: 0; 11: 0; 12: 0; 13: 0; 14: 0; 15: 0; 16: 0; 17: 0; 18: 0; 19: 0; 20: 0; 21: 0; 22: 0; 23: 0; 24: 0; 25: 0; 26: 0; 27: 0
| c) | Ant weed treatment & Site Surfing Cost per Meter | INR Lakhs | 1: 0.00050188; 2: 0; 3: 0; 4: 0; 5: 0; 6: 0; 7: 0; 8: 0; 9: 0; 10: 0; 11: 0; 12: 0; 13: 0; 14: 0; 15: 0; 16: 0; 17: 0; 18: 0; 19: 0; 20: 0; 21: 0; 22: 0; 23: 0; 24: 0; 25: 0; 26: 0; 27: 0
| d) | Road work (Cost per Meter) | INR Lakhs | 1: 0.018213; 2: 0; 3: 0; 4: 0; 5: 0; 6: 0; 7: 0; 8: 0; 9: 0; 10: 0; 11: 0; 12: 0; 13: 0; 14: 0; 15: 0; 16: 0; 17: 0; 18: 0; 19: 0; 20: 0; 21: 0; 22: 0; 23: 0; 24: 0; 25: 0; 26: 0; 27: 0
| e) | Storm water drain, Road culverts drain crossing, cable trench crossing | INR Lakhs | 1: 0.015599; 2: 0; 3: 0; 4: 0; 5: 0; 6: 0; 7: 0; 8: 0; 9: 0; 10: 0; 11: 0; 12: 0; 13: 0; 14: 0; 15: 0; 16: 0; 17: 0; 18: 0; 19: 0; 20: 0; 21: 0; 22: 0; 23: 0; 24: 0; 25: 0; 26: 0; 27: 0
| f) | Switch yard fencing | INR Lakhs | 1: 0.00072; 2: 0; 3: 0; 4: 0; 5: 0; 6: 0; 7: 0; 8: 0; 9: 0; 10: 0; 11: 0; 12: 0; 13: 0; 14: 0; 15: 0; 16: 0; 17: 0; 18: 0; 19: 0; 20: 0; 21: 0; 22: 0; 23: 0; 24: 0; 25: 0; 26: 0; 27: 0
| g) | DG room & Fire fighting Room (FFPH) | INR Lakhs | 1: 56; 2: 0; 3: 0; 4: 0; 5: 0; 6: 0; 7: 0; 8: 0; 9: 0; 10: 0; 11: 0; 12: 0; 13: 0; 14: 0; 15: 0; 16: 0; 17: 0; 18: 0; 19: 0; 20: 0; 21: 0; 22: 0; 23: 0; 24: 0; 25: 0; 26: 0; 27: 0
| h) | Control room with cable vaults | INR Lakhs | 1: 100; 2: 0; 3: 0; 4: 0; 5: 0; 6: 0; 7: 0; 8: 0; 9: 0; 10: 0; 11: 0; 12: 0; 13: 0; 14: 0; 15: 0; 16: 0; 17: 0; 18: 0; 19: 0; 20: 0; 21: 0; 22: 0; 23: 0; 24: 0; 25: 0; 26: 0; 27: 0
| j) | Cable ducts | INR Lakhs | 1: 90; 2: 0; 3: 0; 4: 0; 5: 0; 6: 0; 7: 0; 8: 0; 9: 0; 10: 0; 11: 0; 12: 0; 13: 0; 14: 0; 15: 0; 16: 0; 17: 0; 18: 0; 19: 0; 20: 0; 21: 0; 22: 0; 23: 0; 24: 0; 25: 0; 26: 0; 27: 0
| j) | Providing water supply including drinking water & water for fire fighting system and sewage system | INR Lakhs | 1: 5; 2: 0; 3: 0; 4: 0; 5: 0; 6: 0; 7: 0; 8: 0; 9: 0; 10: 0; 11: 0; 12: 0; 13: 0; 14: 0; 15: 0; 16: 0; 17: 0; 18: 0; 19: 0; 20: 0; 21: 0; 22: 0; 23: 0; 24: 0; 25: 0; 26: 0; 27: 0
| k) | Parking sheds,Rain water Harvesting systems & land scaping etc. | INR Lakhs | 1: 30; 2: 0; 3: 0; 4: 0; 5: 0; 6: 0; 7: 0; 8: 0; 9: 0; 10: 0; 11: 0; 12: 0; 13: 0; 14: 0; 15: 0; 16: 0; 17: 0; 18: 0; 19: 0; 20: 0; 21: 0; 22: 0; 23: 0; 24: 0; 25: 0; 26: 0; 27: 0
| 19 | Erection charges
| a) | Common equipments
|  | Auxiliary Transformers,LT Switchgear, AC & DC Panels.72.5 kV ,33kV & 11 kV equipments etc. | INR Lakhs | 1: 2; 2: 0; 3: 0; 4: 0; 5: 0; 6: 0; 7: 0; 8: 0; 9: 0; 10: 0; 11: 0; 12: 0; 13: 0; 14: 0; 15: 0; 16: 0; 17: 0; 18: 0; 19: 0; 20: 0; 21: 0; 22: 0; 23: 0; 24: 0; 25: 0; 26: 0; 27: 0
|  | Station D.C Batteries 220 V, 500 AH | INR Lakhs | 1: 0.2496; 2: 0; 3: 0; 4: 0; 5: 0; 6: 0; 7: 0; 8: 0; 9: 0; 10: 0; 11: 0; 12: 0; 13: 0; 14: 0; 15: 0; 16: 0; 17: 0; 18: 0; 19: 0; 20: 0; 21: 0; 22: 0; 23: 0; 24: 0; 25: 0; 26: 0; 27: 0
|  | Station D.C Batteries 50 V, 500 AH | INR Lakhs | 1: 0.104; 2: 0; 3: 0; 4: 0; 5: 0; 6: 0; 7: 0; 8: 0; 9: 0; 10: 0; 11: 0; 12: 0; 13: 0; 14: 0; 15: 0; 16: 0; 17: 0; 18: 0; 19: 0; 20: 0; 21: 0; 22: 0; 23: 0; 24: 0; 25: 0; 26: 0; 27: 0
|  | Battery Charger System 220 V, 70A / 50 A Float cum Boost | INR Lakhs | 1: 0.2; 2: 0; 3: 0; 4: 0; 5: 0; 6: 0; 7: 0; 8: 0; 9: 0; 10: 0; 11: 0; 12: 0; 13: 0; 14: 0; 15: 0; 16: 0; 17: 0; 18: 0; 19: 0; 20: 0; 21: 0; 22: 0; 23: 0; 24: 0; 25: 0; 26: 0; 27: 0
|  | Battery Charger System 50 V, 70 A / 50 A Float cum Boost | INR Lakhs | 1: 0.15; 2: 0; 3: 0; 4: 0; 5: 0; 6: 0; 7: 0; 8: 0; 9: 0; 10: 0; 11: 0; 12: 0; 13: 0; 14: 0; 15: 0; 16: 0; 17: 0; 18: 0; 19: 0; 20: 0; 21: 0; 22: 0; 23: 0; 24: 0; 25: 0; 26: 0; 27: 0
|  | Common equipment pertaining to C&R system.( Automation) | INR Lakhs | 1: 7; 2: 0; 3: 0; 4: 0; 5: 0; 6: 0; 7: 0; 8: 0; 9: 0; 10: 0; 11: 0; 12: 0; 13: 0; 14: 0; 15: 0; 16: 0; 17: 0; 18: 0; 19: 0; 20: 0; 21: 0; 22: 0; 23: 0; 24: 0; 25: 0; 26: 0; 27: 0
|  | Power cables | INR Lakhs | 1: 4; 2: 0; 3: 0; 4: 0; 5: 0; 6: 0; 7: 0; 8: 0; 9: 0; 10: 0; 11: 0; 12: 0; 13: 0; 14: 0; 15: 0; 16: 0; 17: 0; 18: 0; 19: 0; 20: 0; 21: 0; 22: 0; 23: 0; 24: 0; 25: 0; 26: 0; 27: 0
|  | Control cables | INR Lakhs | 1: 6; 2: 0; 3: 0; 4: 0; 5: 0; 6: 0; 7: 0; 8: 0; 9: 0; 10: 0; 11: 0; 12: 0; 13: 0; 14: 0; 15: 0; 16: 0; 17: 0; 18: 0; 19: 0; 20: 0; 21: 0; 22: 0; 23: 0; 24: 0; 25: 0; 26: 0; 27: 0
|  | Earth mat 40 mm Rods ( Main Earth Mat) | INR Lakhs | 1: 15; 2: 0; 3: 0; 4: 0; 5: 0; 6: 0; 7: 0; 8: 0; 9: 0; 10: 0; 11: 0; 12: 0; 13: 0; 14: 0; 15: 0; 16: 0; 17: 0; 18: 0; 19: 0; 20: 0; 21: 0; 22: 0; 23: 0; 24: 0; 25: 0; 26: 0; 27: 0
|  | Diesel Generator set with AMF panel 250 kVA | INR Lakhs | 1: 0.6; 2: 0; 3: 0; 4: 0; 5: 0; 6: 0; 7: 0; 8: 0; 9: 0; 10: 0; 11: 0; 12: 0; 13: 0; 14: 0; 15: 0; 16: 0; 17: 0; 18: 0; 19: 0; 20: 0; 21: 0; 22: 0; 23: 0; 24: 0; 25: 0; 26: 0; 27: 0
|  | Air Conditioning and Ventilation | INR Lakhs | 1: 0.9; 2: 0; 3: 0; 4: 0; 5: 0; 6: 0; 7: 0; 8: 0; 9: 0; 10: 0; 11: 0; 12: 0; 13: 0; 14: 0; 15: 0; 16: 0; 17: 0; 18: 0; 19: 0; 20: 0; 21: 0; 22: 0; 23: 0; 24: 0; 25: 0; 26: 0; 27: 0
|  | Fire Fighting System | INR Lakhs | 1: 8; 2: 0; 3: 0; 4: 0; 5: 0; 6: 0; 7: 0; 8: 0; 9: 0; 10: 0; 11: 0; 12: 0; 13: 0; 14: 0; 15: 0; 16: 0; 17: 0; 18: 0; 19: 0; 20: 0; 21: 0; 22: 0; 23: 0; 24: 0; 25: 0; 26: 0; 27: 0
|  | Lightning & lightnening masts | INR Lakhs | 1: 0.9; 2: 0; 3: 0; 4: 0; 5: 0; 6: 0; 7: 0; 8: 0; 9: 0; 10: 0; 11: 0; 12: 0; 13: 0; 14: 0; 15: 0; 16: 0; 17: 0; 18: 0; 19: 0; 20: 0; 21: 0; 22: 0; 23: 0; 24: 0; 25: 0; 26: 0; 27: 0
|  | Illumination System - Indoor & outdoor | INR Lakhs | 1: 10; 2: 0; 3: 0; 4: 0; 5: 0; 6: 0; 7: 0; 8: 0; 9: 0; 10: 0; 11: 0; 12: 0; 13: 0; 14: 0; 15: 0; 16: 0; 17: 0; 18: 0; 19: 0; 20: 0; 21: 0; 22: 0; 23: 0; 24: 0; 25: 0; 26: 0; 27: 0
| b) | ICTs ( Power Transformers) |  | 7: 0; 8: 0; 9: 0; 10: 0; 11: 0; 12: 0; 13: 0; 14: 0; 15: 0; 16: 0; 17: 0; 18: 0; 19: 0; 20: 0; 21: 0; 22: 0; 23: 0; 24: 0; 25: 0; 26: 0; 27: 0
|  | I.C.T 315 MVA, 3Phase, 400/220/33 KV class | INR Lakhs | 1: 6; 2: 0; 3: 0; 4: 0; 5: 0; 6: 0; 7: 0; 8: 0; 9: 0; 10: 0; 11: 0; 12: 0; 13: 0; 14: 0; 15: 0; 16: 0; 17: 0; 18: 0; 19: 0; 20: 0; 21: 0; 22: 0; 23: 0; 24: 0; 25: 0; 26: 0; 27: 0
|  | I.C.T 167 MVA, S-Phase, 400/220 kV ( Single Phase 167 MVA Units) | INR Lakhs | 1: 6; 2: 0; 3: 0; 4: 0; 5: 0; 6: 0; 7: 0; 8: 0; 9: 0; 10: 0; 11: 0; 12: 0; 13: 0; 14: 0; 15: 0; 16: 0; 17: 0; 18: 0; 19: 0; 20: 0; 21: 0; 22: 0; 23: 0; 24: 0; 25: 0; 26: 0; 27: 0
| c) | Shunt & Bus Reactors 400 kV | INR Lakhs | 1: 4; 2: 0; 3: 0; 4: 0; 5: 0; 6: 0; 7: 0; 8: 0; 9: 0; 10: 0; 11: 0; 12: 0; 13: 0; 14: 0; 15: 0; 16: 0; 17: 0; 18: 0; 19: 0; 20: 0; 21: 0; 22: 0; 23: 0; 24: 0; 25: 0; 26: 0; 27: 0
| d) | 400 kV equipments |  | 7: 0; 8: 0; 9: 0; 10: 0; 11: 0; 12: 0; 13: 0; 14: 0; 15: 0; 16: 0; 17: 0; 18: 0; 19: 0; 20: 0; 21: 0; 22: 0; 23: 0; 24: 0; 25: 0; 26: 0; 27: 0
|  | 420 KV Circuit breakers | INR Lakhs | 1: 0.3; 2: 0; 3: 0; 4: 0; 5: 0; 6: 0; 7: 0; 8: 0; 9: 0; 10: 0; 11: 0; 12: 0; 13: 0; 14: 0; 15: 0; 16: 0; 17: 0; 18: 0; 19: 0; 20: 0; 21: 0; 22: 0; 23: 0; 24: 0; 25: 0; 26: 0; 27: 0
|  | 420KV Isolators | INR Lakhs | 1: 0.2; 2: 0; 3: 0; 4: 0; 5: 0; 6: 0; 7: 0; 8: 0; 9: 0; 10: 0; 11: 0; 12: 0; 13: 0; 14: 0; 15: 0; 16: 0; 17: 0; 18: 0; 19: 0; 20: 0; 21: 0; 22: 0; 23: 0; 24: 0; 25: 0; 26: 0; 27: 0
|  | 420 KV Current Transformers | INR Lakhs | 1: 0.06; 2: 0; 3: 0; 4: 0; 5: 0; 6: 0; 7: 0; 8: 0; 9: 0; 10: 0; 11: 0; 12: 0; 13: 0; 14: 0; 15: 0; 16: 0; 17: 0; 18: 0; 19: 0; 20: 0; 21: 0; 22: 0; 23: 0; 24: 0; 25: 0; 26: 0; 27: 0
|  | 420KV CVT | INR Lakhs | 1: 0.06; 2: 0; 3: 0; 4: 0; 5: 0; 6: 0; 7: 0; 8: 0; 9: 0; 10: 0; 11: 0; 12: 0; 13: 0; 14: 0; 15: 0; 16: 0; 17: 0; 18: 0; 19: 0; 20: 0; 21: 0; 22: 0; 23: 0; 24: 0; 25: 0; 26: 0; 27: 0
|  | 390KV surge Arrestors | INR Lakhs | 1: 0.03; 2: 0; 3: 0; 4: 0; 5: 0; 6: 0; 7: 0; 8: 0; 9: 0; 10: 0; 11: 0; 12: 0; 13: 0; 14: 0; 15: 0; 16: 0; 17: 0; 18: 0; 19: 0; 20: 0; 21: 0; 22: 0; 23: 0; 24: 0; 25: 0; 26: 0; 27: 0
|  | Towers , Beams Lattice Type | INR Lakhs | 1: 6.3; 2: 0; 3: 0; 4: 0; 5: 0; 6: 0; 7: 0; 8: 0; 9: 0; 10: 0; 11: 0; 12: 0; 13: 0; 14: 0; 15: 0; 16: 0; 17: 0; 18: 0; 19: 0; 20: 0; 21: 0; 22: 0; 23: 0; 24: 0; 25: 0; 26: 0; 27: 0
|  | Tubular type pipe structures | INR Lakhs | 1: 2; 2: 0; 3: 0; 4: 0; 5: 0; 6: 0; 7: 0; 8: 0; 9: 0; 10: 0; 11: 0; 12: 0; 13: 0; 14: 0; 15: 0; 16: 0; 17: 0; 18: 0; 19: 0; 20: 0; 21: 0; 22: 0; 23: 0; 24: 0; 25: 0; 26: 0; 27: 0
|  | Bus Bars formation etc. | INR Lakhs | 1: 15; 2: 0; 3: 0; 4: 0; 5: 0; 6: 0; 7: 0; 8: 0; 9: 0; 10: 0; 11: 0; 12: 0; 13: 0; 14: 0; 15: 0; 16: 0; 17: 0; 18: 0; 19: 0; 20: 0; 21: 0; 22: 0; 23: 0; 24: 0; 25: 0; 26: 0; 27: 0
| e) | Control & Protection panels |  | 7: 0; 8: 0; 9: 0; 10: 0; 11: 0; 12: 0; 13: 0; 14: 0; 15: 0; 16: 0; 17: 0; 18: 0; 19: 0; 20: 0; 21: 0; 22: 0; 23: 0; 24: 0; 25: 0; 26: 0; 27: 0
|  | 400KV CB relay Panel | INR Lakhs | 1: 0.3; 2: 0; 3: 0; 4: 0; 5: 0; 6: 0; 7: 0; 8: 0; 9: 0; 10: 0; 11: 0; 12: 0; 13: 0; 14: 0; 15: 0; 16: 0; 17: 0; 18: 0; 19: 0; 20: 0; 21: 0; 22: 0; 23: 0; 24: 0; 25: 0; 26: 0; 27: 0
|  | 400KV Line Protection Panel | INR Lakhs | 1: 0.9; 2: 0; 3: 0; 4: 0; 5: 0; 6: 0; 7: 0; 8: 0; 9: 0; 10: 0; 11: 0; 12: 0; 13: 0; 14: 0; 15: 0; 16: 0; 17: 0; 18: 0; 19: 0; 20: 0; 21: 0; 22: 0; 23: 0; 24: 0; 25: 0; 26: 0; 27: 0
|  | 400-220/33KV Transformer Protection Panel | INR Lakhs | 1: 0.54652; 2: 0; 3: 0; 4: 0; 5: 0; 6: 0; 7: 0; 8: 0; 9: 0; 10: 0; 11: 0; 12: 0; 13: 0; 14: 0; 15: 0; 16: 0; 17: 0; 18: 0; 19: 0; 20: 0; 21: 0; 22: 0; 23: 0; 24: 0; 25: 0; 26: 0; 27: 0
|  | 400KV Reactor Protection Panel | INR Lakhs | 1: 0.095568; 2: 0; 3: 0; 4: 0; 5: 0; 6: 0; 7: 0; 8: 0; 9: 0; 10: 0; 11: 0; 12: 0; 13: 0; 14: 0; 15: 0; 16: 0; 17: 0; 18: 0; 19: 0; 20: 0; 21: 0; 22: 0; 23: 0; 24: 0; 25: 0; 26: 0; 27: 0
|  | Duplicate Bus Bar Protection Panel - 400KV | INR Lakhs | 1: 1.5984; 2: 0; 3: 0; 4: 0; 5: 0; 6: 0; 7: 0; 8: 0; 9: 0; 10: 0; 11: 0; 12: 0; 13: 0; 14: 0; 15: 0; 16: 0; 17: 0; 18: 0; 19: 0; 20: 0; 21: 0; 22: 0; 23: 0; 24: 0; 25: 0; 26: 0; 27: 0
|  | PLCC Equipments (Both for 400 kV & 220 kV) | INR Lakhs | 1: 1.25; 2: 0; 3: 0; 4: 0; 5: 0; 6: 0; 7: 0; 8: 0; 9: 0; 10: 0; 11: 0; 12: 0; 13: 0; 14: 0; 15: 0; 16: 0; 17: 0; 18: 0; 19: 0; 20: 0; 21: 0; 22: 0; 23: 0; 24: 0; 25: 0; 26: 0; 27: 0
| f) | 220 kV Equipments | INR Lakhs | 7: 0; 8: 0; 9: 0; 10: 0; 11: 0; 12: 0; 13: 0; 14: 0; 15: 0; 16: 0; 17: 0; 18: 0; 19: 0; 20: 0; 21: 0; 22: 0; 23: 0; 24: 0; 25: 0; 26: 0; 27: 0
|  | 245 KV Circuit breakers | INR Lakhs | 1: 0.2; 2: 0; 3: 0; 4: 0; 5: 0; 6: 0; 7: 0; 8: 0; 9: 0; 10: 0; 11: 0; 12: 0; 13: 0; 14: 0; 15: 0; 16: 0; 17: 0; 18: 0; 19: 0; 20: 0; 21: 0; 22: 0; 23: 0; 24: 0; 25: 0; 26: 0; 27: 0
|  | 245 KV Isolators | INR Lakhs | 1: 0.15; 2: 0; 3: 0; 4: 0; 5: 0; 6: 0; 7: 0; 8: 0; 9: 0; 10: 0; 11: 0; 12: 0; 13: 0; 14: 0; 15: 0; 16: 0; 17: 0; 18: 0; 19: 0; 20: 0; 21: 0; 22: 0; 23: 0; 24: 0; 25: 0; 26: 0; 27: 0
|  | 245 KV Current Transformers | INR Lakhs | 1: 0.05; 2: 0; 3: 0; 4: 0; 5: 0; 6: 0; 7: 0; 8: 0; 9: 0; 10: 0; 11: 0; 12: 0; 13: 0; 14: 0; 15: 0; 16: 0; 17: 0; 18: 0; 19: 0; 20: 0; 21: 0; 22: 0; 23: 0; 24: 0; 25: 0; 26: 0; 27: 0
|  | 245 KV CVT | INR Lakhs | 1: 0.05; 2: 0; 3: 0; 4: 0; 5: 0; 6: 0; 7: 0; 8: 0; 9: 0; 10: 0; 11: 0; 12: 0; 13: 0; 14: 0; 15: 0; 16: 0; 17: 0; 18: 0; 19: 0; 20: 0; 21: 0; 22: 0; 23: 0; 24: 0; 25: 0; 26: 0; 27: 0
|  | 216 KV surge Arrestors | INR Lakhs | 1: 0.03; 2: 0; 3: 0; 4: 0; 5: 0; 6: 0; 7: 0; 8: 0; 9: 0; 10: 0; 11: 0; 12: 0; 13: 0; 14: 0; 15: 0; 16: 0; 17: 0; 18: 0; 19: 0; 20: 0; 21: 0; 22: 0; 23: 0; 24: 0; 25: 0; 26: 0; 27: 0
| h) | 220 kV Towers & beams | INR Lakhs | 1: 6; 2: 0; 3: 0; 4: 0; 5: 0; 6: 0; 7: 0; 8: 0; 9: 0; 10: 0; 11: 0; 12: 0; 13: 0; 14: 0; 15: 0; 16: 0; 17: 0; 18: 0; 19: 0; 20: 0; 21: 0; 22: 0; 23: 0; 24: 0; 25: 0; 26: 0; 27: 0
| i) | 220 tubular pipe structures | INR Lakhs | 1: 3; 2: 0; 3: 0; 4: 0; 5: 0; 6: 0; 7: 0; 8: 0; 9: 0; 10: 0; 11: 0; 12: 0; 13: 0; 14: 0; 15: 0; 16: 0; 17: 0; 18: 0; 19: 0; 20: 0; 21: 0; 22: 0; 23: 0; 24: 0; 25: 0; 26: 0; 27: 0
| j) | 220 kV Bus Bars formation etc | INR Lakhs | 1: 16; 2: 0; 3: 0; 4: 0; 5: 0; 6: 0; 7: 0; 8: 0; 9: 0; 10: 0; 11: 0; 12: 0; 13: 0; 14: 0; 15: 0; 16: 0; 17: 0; 18: 0; 19: 0; 20: 0; 21: 0; 22: 0; 23: 0; 24: 0; 25: 0; 26: 0; 27: 0
| k) | Control & Protection panels |  | 7: 0; 8: 0; 9: 0; 10: 0; 11: 0; 12: 0; 13: 0; 14: 0; 15: 0; 16: 0; 17: 0; 18: 0; 19: 0; 20: 0; 21: 0; 22: 0; 23: 0; 24: 0; 25: 0; 26: 0; 27: 0
|  | Circuit breaker relay panel With Auto reclosure | INR Lakhs | 1: 0.25; 2: 0; 3: 0; 4: 0; 5: 0; 6: 0; 7: 0; 8: 0; 9: 0; 10: 0; 11: 0; 12: 0; 13: 0; 14: 0; 15: 0; 16: 0; 17: 0; 18: 0; 19: 0; 20: 0; 21: 0; 22: 0; 23: 0; 24: 0; 25: 0; 26: 0; 27: 0
|  | Line protection panel | INR Lakhs | 1: 0.66; 2: 0; 3: 0; 4: 0; 5: 0; 6: 0; 7: 0; 8: 0; 9: 0; 10: 0; 11: 0; 12: 0; 13: 0; 14: 0; 15: 0; 16: 0; 17: 0; 18: 0; 19: 0; 20: 0; 21: 0; 22: 0; 23: 0; 24: 0; 25: 0; 26: 0; 27: 0
|  | Single Bus Bar protection panel | INR Lakhs | 1: 2; 2: 0; 3: 0; 4: 0; 5: 0; 6: 0; 7: 0; 8: 0; 9: 0; 10: 0; 11: 0; 12: 0; 13: 0; 14: 0; 15: 0; 16: 0; 17: 0; 18: 0; 19: 0; 20: 0; 21: 0; 22: 0; 23: 0; 24: 0; 25: 0; 26: 0; 27: 0

## Escalated Cost
CERC
Capital Cost Benchmarking
| Month and Year of Escalation |  | 2009-12-01
Project Costs (Escalated)
|  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65
|  | Name of the Utility |  | PGCIL | PGCIL | PGCIL | PGCIL | PGCIL | PGCIL | PGCIL | PGCIL | PGCIL | PGCIL | PGCIL | PGCIL | PGCIL | PGCIL | PGCIL | PGCIL | PGCIL | PGCIL | PGCIL | PGCIL | RVPN | APTRANSCO | MSETCL | MSETCL | MSETCL | NSPCL -Sail power company for Bilai steel plant | PGCIL | PGCIL | PGCIL | PGCIL | PGCIL | PGCIL | PGCIL | PGCIL | PGCIL | PGCIL | PGCIL | PGCIL | PGCIL | PGCIL | PGCIL | PGCIL | PGCIL | PGCIL | PGCIL | PGCIL | PGCIL | PGCIL | PGCIL | PGCIL | PGCIL | PGCIL | PGCIL | PGCIL | PGCIL | PGCIL | PGCIL | PGCIL | PGCIL | PGCIL | PGCIL | PGCIL | PGCIL | PGCIL | PGCIL
|  | Name of sub-station |  | 400/220 kV S/S, ARASUR(New) | 400/220 kV S/S AT,ROORKEE | 400/220 kV S/S, PUGALUR(New) | 400/220 kV S/S, DAMOH (New) | 400/220 kV S/S, KARAIKUDI(New) | 400/220 kV S/S AT, WARANGAL | Kankroli | Kaithal | Tirunelveli | Shubashgram | Raigarh | Amritsar | Kolar,Munirabad & Somanahalli extn works | Ludhiyana, Extn of Jalandhar & Malerakotla | Fatehabad | Gwalior | Patna | Muzaffarpur & Biharsheriff | Narendra | Melakottaiyur | Jaisalmer -Rajasthan State | Malkaram - A.P.TRANSCO | Koradi- Maharastra | Khaparkheda - MSETCL- Maharastra | Chakan- MSETCL- Maharastra | NSPCL -Sail power company for Bilai steel plant | Shulajpur(New), Dehgam & VAPI (Extn Works) | Mandola,MalerakotlaBiharsherief, Hyderabad & Durgapaur | (Extn Works), GWALIOR, WARDHA, PUNE, RAIPUR | Pirana,Gwaliar & Bina | GIS New Delhi | Gwalior | Batapara | Amritsar | Navi Mumbai | Kota | Kankroli | Ludhiyana | Fathebad | Moga | Sonepat | Khandwa | Dehgan | 765 kV & 400 kV pooling station- Bihar sherief (Balia,Phathepur, Agra, Lucknow) | Ludhiyana | Trivandrum, & Madurai | Udamalpet & Trichi | Fathebad | Patna | Ranchi | Bihar Sharif | Shujalpur | Kankroli | Kota | Bihar Sharif,Sasaram & Ranchi | Gaya, DVC & Maithon | Lucknow | Agra | Fatepur | Balia | Allahabad | Itarsi | Vijayawada | Rourkela | Tiruvanneli
|  | Reference P.O. No. |  | Ref:- LOA-55803-S119A-7/LOA-1/1986 &1987 Dated 10-03-2006 | Ref-C-13901-S919A-3/LOA-I/2198 & 2199 DATED 01/11/2006 | Ref:- LOA C-55802-S119A-7/LOA-1/1966 &1967(Proj-1) Dated 24/02/06 | Ref:- LOA C-56204-S919A-3/LOA-I/2025 & 2026 DATED:20/04/06 | Ref:- LOA C-56301-S919A-3/LOA-II/2128&2129 dated 23-08-2006 | Ref-C-55807-S119A-7/LOA-I-2020 & 2021 DATED 31/03/2006 | C-13502-S919A-3/LOA-I/1905 & 2021 DT: 16/01/2006 | C-1128-S948-3/LOA-I/1064 DT: 28/03/2003 | C-52705-S919A-3/LOA-II/1842 DT: 02/11/2005 | C-42406-S919A-3/LOA-I/1237 & 1238 DT: 30/01/2004 | C-32306-S919A-3/LOA-I/1424 DT: 11/10/2004 | C-21501-S919A-3/LOA-I/1349 & 1350 | LTCD/EIC/PGCIL/56004/ONLN /2005/101 | C-21702-S919A-3/LOA-I/1759 | C-21703-S919A-3/LOA-I/1718 | .C-324054-S919-3/LOA-I/1549 DT: 14-03-05 | :C-45907-S919A-3/L0A-I/1708 | C-42407-S919A-3/LOA-I/1294 DT: 29/03/2004 | C-55102-S919A-3/LOA-1/1208 dt: 31/12/2003: | C-56103-S919A-3/LOA-I/1921 dated 31/01/2006 | RVPN:400 kV Design/Xtn(Tr)/TN-231/Supply/PO274/D.1236. Jaipur Dt:22-04-08 | OM - 0332 CE/Const./400KV/SE.PM-II/D2-A1/MLKM/Supply/D. No. 604/2008 Dated - 20/09/2008 - Supply of Equipments and Material | REF: TBMS/08/E1036/PD Rev 01 DT 12.5.09 | REF: No.MSETCL/CO/Tr. Proj./TKP/2007-08/23 DT: 30-11-07 | REF: No.MSETCL/CO/Tr. Proj./TKP/2007-08/23 DT: 30-11-07 |  | 55701-S116-3/LOA-1/2582 &2583 Dated 14-07-2008 | C-00703 -S-916-3/LOA-1/2340: DT:18-04-2007 | 33501-S116-3/LOA-I/2534 DT: 02-05-2008 : | C-33501-S116-3/LOA-1/2534 & 2535 Dt:02-05-2008 | C-41414-S919 A-I/1553 DT:29-03-2005 : | C-32404-S116-3I/1LOA/1582 DT: 24-03-2005 : | C-32404-S116-3I/1LOA/1582 DT: 24-03-2005 : | C-22101-S916-3/LOA/1980 DT: 02-03-2006 | C-33402-S119A-3/LOA-II/2472 DT:20/03/2008: | C-13501-S917-3/LOA/1730 | C-13501-S917-3/LOA/1730 | C-21702-S916-3/LOA/1535 DT: 07-03-2005 : | C-21702-S916-3/LOA/1535 DT: 07-03-2005 : | C-22101-S916-3/LOA/1980 DT: 02-03-2006 : |  | C-33601-S117-7/LOA-I/2458 & LOA -II / 2459 DT:05-03-2008 : | C-33601-S117-7/LOA-I/2458 & LOA -II / 2459 DT:05-03-2008 : | C-14803-S117-3/LOA-1/2708: DT:22-10-2008 : | C-21702-S917-3/LOA/1664 DT: 04-05-2005 : | C -56401 - S117 - 3 / LOA - 1 / 2478 DT: 25 - 03 - 2008 : | C -56401 - S117 - 3 / LOA - 1 / 2478 DT: 25 - 03 - 2008 : | C-21702-S917-3/LOA/1664 DT: 04-05-2005 | C-45906-S917-3/LOA/1438 DT: 20-10-2004 : | C-45906-S917-3/LOA/1438 DT: 20-10-2004 | C-45906-S917-3/LOA/1438 DT: 20-10-2004 : | C -33701 - S117 - 3 / P-165/LOA-1/2584 & 2585 DT: 14 - 07 - 2008 : | C-13501-S917-3/LOA/1730 Dt:18-10-04 | C-13501-S917-3/LOA/1730 Dt:18-10-04 | C -47208 - S117 - 3 / LOA - 1 / 2706 DT: 22 -10 - 2008 | C -47208 - S117 - 3 / LOA - 1 / 2706 DT: 22 -10 - 2008 | C -47208 - S117 - 3 / LOA - 1 / 2706 DT: 22 -10 - 2008 | C -47208 - S117 - 3 / LOA - 1 / 2706 DT: 22 -10 - 2008 | C -14803 - S117 - 3 / LOA - 1 / 2708 & 2709 DT:22 - 10 - 2008 : | C -14803 - S117 - 3 / LOA - 1 / 2708 & 2709 DT:22 - 10 - 2008 : | C -00704 - S917 - 3 / LOA - 1 / 2365 & 2366 DT: 25 - 06 - 2007 | C -00704 - S917 - 3 / LOA - 1 / 2365 & 2366 DT: 25 - 06 - 2007 | C -00704 - S917 - 3 / LOA - 1 / 2365 & 2366 DT: 25 - 06 - 2007 | C -00704 - S917 - 3 / LOA - 1 / 2365 & 2366 DT: 25 - 06 - 2007 | C-45906-S917-3/L0A/1438 DT:13-06-2005:
|  | Base Data of Indices |  | 2005-08-01 | 2006-04-01 | 2005-08-01 | 2006-01-01 | 2006-04-01 | 2005-08-01 | 2005-05-01 | 2002-06-01 | 2005-05-01 | 2003-08-01 | 2004-03-01 | 2003-08-01 | 2004-11-01 | 2004-09-01 | 2004-09-01 | 2004-09-01 | 2004-08-01 | 2003-08-01 | 2003-08-01 | 2005-05-01 | 2007-10-01 | 2008-03-01 | 2009-01-01 | 2007-10-01 | 2007-10-01 | 2005-08-01 | 2007-12-01 | 2006-12-01 | 2007-07-01 | 2007-07-01 | 2004-08-01 | 2004-08-01 | 2004-08-01 | 2005-09-01 | 2007-11-01 | 2004-09-01 | 2004-09-01 | 2004-07-01 | 2004-07-01 | 2005-09-01 | 2007-09-01 | 2007-08-01 | 2007-08-01 | 2007-08-01 | 2004-07-01 | 2007-09-01 | 2007-09-01 | 2004-07-01 | 2004-03-01 | 2004-03-01 | 2004-03-01 | 2007-12-01 | 2005-01-01 | 2004-09-01 | 2008-04-01 | 2008-04-01 | 2008-04-01 | 2008-04-01 | 2008-04-01 | 2008-04-01 | 2006-12-01 | 2006-12-01 | 2006-12-01 | 2006-12-01 | 2005-05-01
| S.No. | Name of the Component | Unit
| 1 | Power Transformer
| a) | ICT 400/√3/220 √3/ 33KV,167 MVA, single phase autotransformer including Insulating Oil Frieght & Insurance | INR Lakhs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 488.9265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) | I.C.T 315 MVA, 3 Phase, 400/220/33 KV including including Insulating Oil Frieght & Insurance | INR Lakhs | 816.2447 | 0 | 925.221 | 0 | 0 | 956.4421 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 734.95 | 0 | 0 | 0 | 914.8272 | 833.0792 | 905.1109 | 830.0364 | 861.9895 | 894.3531 | 889.394 | 896.6552 | 866.9001 |  | 864.1663 | 865.1092 | 878.3511 | 878.3511 | 0 | 848.2566 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| c) | ICT 400/√3/220 √3/ 33KV,105 MVA, single phase autotransformer including Insulating Oil Frieght & Insurance | INR Lakhs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 389.9462 | 388.7051 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| d) | I.C.T 250 MVA, 3 Phase, 400/220/33 KV including including Insulating Oil Frieght & Insurance |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 786.5113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2 | Shunt Reactor
| a) | 420KV, 125 MVAR, 3-Phase Shunt Reactor | INR Lakhs | 42: 427.9536; 43: 432.1492; 44: 339.0588; 45: 0; 46: 0; 47: 0; 48: 0; 49: 0; 50: 0; 51: 0; 52: 0; 53: 0; 54: 0; 55: 397.3648; 56: 396.5397; 57: 393.4334; 58: 392.3171; 59: 392.3171; 60: 396.2; 61: 0; 62: 0; 63: 0; 64: 0; 65: 0
| b) | 420KV, 80 MVAR, 3-Phase Shunt Reactor | INR Lakhs | 42: 0; 43: 0; 44: 0; 45: 0; 46: 0; 47: 0; 48: 367.5851; 49: 362.8791; 50: 380.8352; 51: 396.2857; 52: 0; 53: 0; 54: 423.9775; 55: 0; 56: 0; 57: 0; 58: 0; 59: 337.4713; 60: 0; 61: 0; 62: 0; 63: 0; 64: 0; 65: 0
| c) | 420KV, 63/50 MVAR, 3-Phase Shunt Reactor | INR Lakhs | 42: 0; 43: 0; 44: 0; 45: 415.9516; 46: 357.4101; 47: 353.7805; 48: 349.8508; 49: 342.4176; 50: 0; 51: 0; 52: 347.3446; 53: 360.0137; 54: 0; 55: 311.5045; 56: 312.815; 57: 0; 58: 309.7087; 59: 0; 60: 0; 61: 315.6776; 62: 310.1217; 63: 315.1726; 64: 319.2132; 65: 387.0476
| d) | NGR with oil, for above 400 kV Shunt Reactor | INR Lakhs | 42: 0; 43: 0; 44: 24.8765; 45: 0; 46: 0; 47: 0; 48: 0; 49: 27.7275; 50: 0; 51: 0; 52: 24.2382; 53: 27.0202; 54: 0; 55: 22.909; 56: 22.9576; 57: 0; 58: 22.7634; 59: 22.7634; 60: 0; 61: 0; 62: 0; 63: 0; 64: 0; 65: 23.5876
| e) | Surge Arrestors 120 kV for NGR | INR Lakhs | 42: 0; 43: 0; 44: 0.92219; 45: 0; 46: 0; 47: 0; 48: 0; 49: 1.7255; 50: 0; 51: 0; 52: 1.2609; 53: 2.4564; 54: 0; 55: 1.2609; 56: 1.2609; 57: 0; 58: 1.2609; 59: 1.2609; 60: 0; 61: 0; 62: 0; 63: 0; 64: 0; 65: 2.9865
| f) | Spares for NGR &120KV SA | INR Lakhs | 42: 0; 43: 0; 44: 0; 45: 0; 46: 0; 47: 0; 48: 0; 49: 0; 50: 0; 51: 0; 52: 0; 53: 0; 54: 0; 55: 0; 56: 0; 57: 0; 58: 0; 59: 0; 60: 0; 61: 0; 62: 0; 63: 0; 64: 0; 65: 0
| 3 | Bus Reactor
| a) | 125 MVAR 400 kV | INR Lakhs
| b) | 80 MVAR 400 kV | INR Lakhs
| c) | 63 / 50 MVAR 400 kV | INR Lakhs
| d) | 50 MVAR | INR Lakhs
| e) | Oil for shunt Reactor | INR Lakhs
| f) | Spares for Bus Reactor | INR Lakhs
| 4 | 420 kV Equipments
| a) | 420 kV Breakers with CR | INR Lakhs | 1: 0; 2: 0; 3: 0; 4: 41.1213; 5: 0; 6: 0; 7: 53.5728; 8: 0; 9: 41.8272; 10: 48.5565; 11: 42.9801; 12: 0; 13: 0; 14: 0; 15: 0; 16: 52.7556; 17: 54.5799; 18: 0; 19: 0; 20: 0; 21: 0; 22: 0; 23: 0; 24: 40.6308; 25: 38.0256; 26: 48.3485
| b) | 420 kVBreakers without CR | INR Lakhs | 1: 42.1547; 2: 41.2168; 3: 39.3405; 4: 32.3986; 5: 30.0003; 6: 40.1161; 7: 61.4547; 8: 51.8612; 9: 37.2535; 10: 45.2078; 11: 39.3771; 12: 48.3033; 13: 45.7302; 14: 46.2737; 15: 36.5201; 16: 44.7044; 17: 39.8853; 18: 71.5066; 19: 40.7519; 20: 52.906; 21: 28.2959; 22: 33.3726; 23: 31.4569; 24: 40.6308; 25: 38.0256; 26: 43.7341
| c) | 420 kV CTs 2000A, 40KA, 5-Core, | INR Lakhs | 1: 6.913; 2: 8.7187; 3: 5.9807; 4: 6.1059; 5: 5.6539; 6: 9.1753; 7: 9.629; 8: 5.6965; 9: 6.8606; 10: 8.3799; 11: 6.6849; 12: 9.0703; 13: 7.9738; 14: 8.2559; 15: 6.4612; 16: 7.9693; 17: 7.8847; 18: 8.3117; 19: 7.5087; 20: 9.2822; 21: 5.4763; 22: 7.2404; 23: 6.934; 24: 7.72; 25: 7.2308; 26: 8.1719
| d) | 420 kv CVT 4400 PF | INR Lakhs | 1: 4.0255; 2: 6.6751; 3: 3.8797; 4: 3.676; 5: 3.577; 6: 6.2394; 7: 6.9483; 8: 4.0128; 9: 5.7498; 10: 6.7039; 11: 5.3521; 12: 7.0088; 13: 0; 14: 6.864; 15: 3.9329; 16: 6.6495; 17: 5.1216; 18: 9.5815; 19: 4.6076; 20: 6.7349; 21: 3.8281; 22: 4.4517; 23: 4.1401; 24: 4.9446; 25: 4.6256; 26: 6.535
| e) | 420 kv CVT 8800 PF | INR Lakhs | 1: 0; 2: 0; 3: 0; 4: 0; 5: 0; 6: 0; 7: 0; 8: 0; 9: 0; 10: 0; 11: 0; 12: 0; 13: 0; 14: 0; 15: 0; 16: 6.8105; 17: 0; 18: 0; 19: 0; 20: 0; 21: 0; 22: 0; 23: 0; 24: 0; 25: 0; 26: 0
| f) | 420 KV,2000 A,40 kA Isolators 3-Phase with one E/S (3 Phase) with insulators | INR Lakhs | 1: 7.6435; 2: 6.1975; 3: 7.9915; 4: 9.621; 5: 5.4534; 6: 7.4115; 7: 10.6559; 8: 10.3097; 9: 8.7888; 10: 12.385; 11: 10.0473; 12: 15.1721; 13: 8.3146; 14: 10.5484; 15: 11.8311; 16: 10.1799; 17: 11.4451; 18: 14.8587; 19: 14.43; 20: 11.7628; 21: 9.1342; 22: 6.7942; 23: 5.8291; 24: 4.3385; 25: 0; 26: 5.246
| g) | 420 KV,2000A,40 kA Isolators 3-Phase with two E/S with insulators | INR Lakhs | 1: 8.8422; 2: 7.5303; 3: 9.216; 4: 11.0376; 5: 8.3411; 6: 8.8035; 7: 12.603; 8: 12.2285; 9: 10.2958; 10: 14.4464; 11: 11.5887; 12: 16.7388; 13: 0; 14: 12.3224; 15: 13.7961; 16: 11.8448; 17: 13.0743; 18: 0; 19: 16.5244; 20: 13.6299; 21: 10.2826; 22: 8.0313; 23: 6.7054; 24: 5.3487; 25: 0; 26: 5.9807
| h) | 420 KV,2000A,40 kA Isolators one Phase with one E/S | INR Lakhs | 1: 0; 2: 0; 3: 0; 4: 0; 5: 0; 6: 0; 7: 0; 8: 0; 9: 0; 10: 0; 11: 0; 12: 0; 13: 2.767; 14: 0; 15: 0; 16: 0; 17: 0; 18: 0; 19: 0; 20: 0; 21: 0; 22: 0; 23: 1.943; 24: 2.1799; 25: 0; 26: 0
| j) | Surge Arrestors 390 kV | INR Lakhs | 1: 1.1343; 2: 1.2217; 3: 2.1268; 4: 1.7471; 5: 1.0885; 6: 1.2761; 7: 1.9205; 8: 2.5643; 9: 1.7642; 10: 2.4675; 11: 1.8259; 12: 2.1439; 13: 1.8537; 14: 2.0606; 15: 2.0196; 16: 1.9923; 17: 2.2863; 18: 4.4527; 19: 2.9355; 20: 1.8538; 21: 1.0846; 22: 1.3183; 23: 1.2827; 24: 1.5844; 25: 1.4781; 26: 1.2761
| 5 | 400 kV Control and Protection Panel
| a) | Circuit Breaker panel with Auto Reclose | INR Lakhs | 1: 7.59; 2: 0; 3: 6.4634; 4: 6.44; 5: 5.3593; 6: 9.7854; 7: 10.84; 8: 1.4413; 9: 10.4546; 10: 2.59; 11: 3.5035; 12: 2.219; 13: 0; 14: 21.48; 15: 8.291; 16: 20.7796; 17: 4.2578; 18: 0; 19: 2.6706; 20: 11.1874; 21: 13.71; 22: 6.7; 23: 10.54; 24: 0; 25: 0; 26: 0
| b) | Circuit Breaker panel without Auto Reclose | INR Lakhs | 1: 6.28; 2: 0; 3: 5.2334; 4: 6.44; 5: 5.6121; 6: 8.172; 7: 9.04; 8: 1.1316; 9: 9.7268; 10: 5.26; 11: 1.9371; 12: 1.5022; 13: 0; 14: 15.82; 15: 8.138; 16: 15.2946; 17: 3.2234; 18: 0; 19: 1.9373; 20: 9.6366; 21: 0; 22: 4.54; 23: 0; 24: 0; 25: 0; 26: 0
| c) | Line protection panel | INR Lakhs | 1: 35.67; 2: 0; 3: 27.2149; 4: 13.58; 5: 13.2971; 6: 18.2784; 7: 15.03; 8: 10.602; 9: 17.988; 10: 16.9; 11: 15.6788; 12: 23.5417; 13: 0; 14: 24.54; 15: 20.3833; 16: 23.6787; 17: 30.3171; 18: 0; 19: 16.3716; 20: 18.7508; 21: 16.0707; 22: 14.74; 23: 22.18; 24: 20.36; 25: 16.94; 26: 0
| d) | Transformer protection panel(both HV and MV) | INR Lakhs | 1: 19.71; 2: 0; 3: 17.0115; 4: 18.76; 5: 17.1901; 6: 11.6122; 7: 12.83; 8: 5.2082; 9: 27.6636; 10: 9.8; 11: 8.5587; 12: 6.0186; 13: 0; 14: 19.82; 15: 20.7765; 16: 19.1139; 17: 19.1711; 18: 0; 19: 9.3782; 20: 11.7769; 21: 16.39; 22: 17.87; 23: 25.19; 24: 26.1; 25: 0; 26: 0
| e) | Reactor protection panel | INR Lakhs | 1: 0; 2: 0; 3: 0; 4: 13.63; 5: 12.5387; 6: 0; 7: 13.12; 8: 0; 9: 13.6729; 10: 0; 11: 6.4227; 12: 0; 13: 0; 14: 14.82; 15: 13.4468; 16: 14.3748; 17: 13.5178; 18: 0; 19: 0; 20: 8.5858; 21: 11.1; 22: 0; 23: 0; 24: 0; 25: 0; 26: 0
| f) | Bus Bar Protection Panel | INR Lakhs | 1: 107.73; 2: 0; 3: 181.7768; 4: 159.75; 5: 96.366; 6: 68.2813; 7: 133.64; 8: 5.16; 9: 210.46; 10: 29.66; 11: 89.02; 12: 16.94; 13: 0; 14: 244.09; 15: 107.4546; 16: 234.94; 17: 181.9648; 18: 0; 19: 6.1789; 20: 123.2905; 21: 109.3; 22: 44.16; 23: 133.58; 24: 37.9; 25: 35.69; 26: 0
| 6 | 245 kV Equipment
| a) | Circuit Breakers 245 kV
|  | 1600 A, 40 kA | INR Lakhs | 1: 15.4932; 2: 17.7373; 3: 18.6756; 4: 15.5763; 5: 14.4232; 6: 16.4197; 7: 16.6173; 8: 19.0493; 9: 16.1042; 10: 19.828; 11: 17.078; 12: 19.9546; 13: 19.3689; 14: 20.087; 15: 16.8554; 16: 19.5336; 17: 17.2836; 18: 0; 19: 19.4374; 20: 21.9919; 21: 12.3456; 22: 14.1765; 23: 14.2743; 24: 17.0669; 25: 15.9716; 26: 18.0969
|  | 2500 A, 40 kA | INR Lakhs | 1: 15.4932; 2: 18.6592; 3: 18.6756; 4: 15.5763; 5: 14.4232; 6: 16.4197; 7: 16.6173; 8: 19.0493; 9: 16.1042; 10: 21.0402; 11: 17.1554; 12: 19.9546; 13: 19.3689; 14: 20.087; 15: 16.8554; 16: 19.5336; 17: 17.2836; 18: 0; 19: 19.4374; 20: 21.9919; 21: 0; 22: 14.1765; 23: 0; 24: 0; 25: 0; 26: 18.1098
| b) | Current Transformers 245 kV |  | 2: 0; 3: 0; 4: 0; 6: 0; 7: 0; 8: 0; 9: 0; 10: 0; 11: 0; 12: 0; 13: 0; 14: 0; 15: 0; 16: 0; 17: 0; 18: 0; 19: 0; 20: 0; 21: 0; 22: 0; 23: 0; 24: 0; 25: 0; 26: 0
|  | 1600 A, 40 kA , 5 core, with 120% extended current | INR Lakhs | 1: 3.5131; 2: 3.7096; 3: 2.9646; 4: 3.1153; 5: 2.8846; 6: 4.4403; 7: 5.0545; 8: 3.1608; 9: 3.3323; 10: 3.8547; 11: 3.3129; 12: 3.3807; 13: 4.0346; 14: 3.8755; 15: 3.2306; 16: 3.7457; 17: 3.8761; 18: 0; 19: 3.3789; 20: 4.7617; 21: 0; 22: 3.7419; 23: 4.4216; 24: 0; 25: 0; 26: 0
|  | 1600 A, 40 kA, 5 core, with 150% extended current | INR Lakhs | 1: 3.6566; 2: 3.7096; 3: 3.1321; 4: 3.1776; 5: 2.9423; 6: 4.5193; 7: 5.1346; 8: 3.3309; 9: 3.3323; 10: 4.0223; 11: 3.3572; 12: 3.4137; 13: 0; 14: 3.8755; 15: 3.329; 16: 3.7457; 17: 4.0914; 18: 0; 19: 4.0734; 20: 4.8388; 21: 0; 22: 0; 23: 4.9785; 24: 4.4023; 25: 4.1152; 26: 5.8389
| c) | Capacitive Voltage Transformer 245 kV |  | 2: 0; 3: 0; 4: 0; 6: 0; 7: 0; 8: 0; 9: 0; 10: 0; 11: 0; 12: 0; 13: 0; 14: 0; 15: 0; 16: 0; 17: 0; 18: 0; 19: 0; 20: 0; 21: 0; 22: 0; 23: 0; 24: 0; 25: 0; 26: 0
|  | 8800 pf, S- Ph, with 3 secondaries | INR Lakhs | 1: 0; 2: 0; 3: 0; 4: 0; 5: 0; 6: 0; 7: 0; 8: 0; 9: 0; 10: 0; 11: 0; 12: 0; 13: 0; 14: 0; 15: 0; 16: 0; 17: 0; 18: 0; 19: 0; 20: 0; 21: 0; 22: 0; 23: 0; 24: 0; 25: 0; 26: 0
|  | 4400 pf, S- Ph with 3 secondaries | INR Lakhs | 1: 3.0694; 2: 3.954; 3: 2.6939; 4: 2.6168; 5: 2.4231; 6: 3.2628; 7: 3.7476; 8: 3.1274; 9: 3.3323; 10: 4.0223; 11: 3.2257; 12: 3.826; 13: 4.0346; 14: 3.6162; 15: 2.5985; 16: 3.4796; 17: 3.5282; 18: 0; 19: 2.867; 20: 3.6775; 21: 2.6584; 22: 3.245; 23: 0; 24: 0; 25: 0; 26: 4.3824
| d) | Isolators 245 kV
|  | 1600A, 40 kA, DB Type with two E/S | INR Lakhs | 1: 3.8345; 2: 3.9018; 3: 3.7684; 4: 4.6833; 5: 2.5814; 6: 3.5965; 7: 4.9612; 8: 5.024; 9: 4.2944; 10: 5.6401; 11: 5.1848; 12: 5.4092; 13: 3.9392; 14: 4.8716; 15: 4.8853; 16: 4.7215; 17: 5.038; 18: 0; 19: 6.1843; 20: 5.1746; 21: 5.019; 22: 3.7216; 23: 0; 24: 0; 25: 0; 26: 4.0857
|  | 1600A, 40 kA, DB Type with one E/S | INR Lakhs | 1: 3.2527; 2: 3.2911; 3: 3.3188; 4: 3.9711; 5: 1.8337; 6: 3.0808; 7: 4.241; 8: 4.239; 9: 3.7342; 10: 4.799; 11: 4.4141; 12: 4.6506; 13: 3.244; 14: 4.1893; 15: 5.8806; 16: 4.0529; 17: 4.3261; 18: 0; 19: 5.1453; 20: 4.4811; 21: 4.0408; 22: 3.2754; 23: 4.0639; 24: 1.7758; 25: 0; 26: 3.3453
|  | 1600A, 40 kA, DB, Tandem Type without E/S | INR Lakhs | 1: 2.737; 2: 2.703; 3: 2.9354; 4: 4.5746; 5: 2.8484; 6: 2.618; 7: 4.5344; 8: 3.5063; 9: 3.2408; 10: 3.9909; 11: 3.6434; 12: 4.1723; 13: 0; 14: 4.0119; 15: 4.1347; 16: 3.3979; 17: 3.6006; 18: 0; 19: 4.2548; 20: 3.8276; 21: 0; 22: 0; 23: 3.6321; 24: 1.2122; 25: 0; 26: 2.7635
|  | 2500A, 40 KA, DB Type with Two E/S | INR Lakhs | 1: 3.9931; 2: 4.1054; 3: 3.9535; 4: 4.9367; 5: 2.2889; 6: 3.7155; 7: 5.2146; 8: 5.1112; 9: 4.5077; 10: 5.7885; 11: 5.3389; 12: 6.2173; 13: 0; 14: 4.9808; 15: 5.8405; 16: 4.8307; 17: 5.1749; 18: 0; 19: 6.0688; 20: 5.4146; 21: 0; 22: 0; 23: 0; 24: 0; 25: 0; 26: 4.1518
|  | 1600A, 40 kA with one E/S S-phase | INR Lakhs | 1: 0; 2: 0; 3: 0; 4: 0; 5: 0; 6: 0; 7: 0; 8: 0; 9: 0; 10: 0; 11: 0; 12: 0; 13: 1.7311; 14: 0; 15: 0; 16: 0; 17: 0; 18: 0; 19: 0; 20: 0; 21: 0; 22: 0; 23: 0; 24: 0; 25: 0; 26: 0
|  | 1600A, 40 kA without E/S S phase | INR Lakhs | 1: 0; 2: 0; 3: 0; 4: 0; 5: 0; 6: 0; 7: 0; 8: 0; 9: 0; 10: 0; 11: 0; 12: 0; 13: 1.1722; 14: 0; 15: 0; 16: 0; 17: 0; 18: 0; 19: 0; 20: 0; 21: 0; 22: 0; 23: 0; 24: 0; 25: 0; 26: 0
| e) | 216 kV Surge Arrestors | INR Lakhs | 1: 0.50245; 2: 0.5994; 3: 0.78012; 4: 0.66387; 5: 0.71209; 6: 0.68756; 7: 1.0002; 8: 1.0816; 9: 0.79715; 10: 0.96936; 11: 0.86866; 12: 0.74211; 13: 0.93561; 14: 0.8597; 15: 0.80512; 16: 0.83241; 17: 0.78035; 18: 0; 19: 1.0884; 20: 0.96023; 21: 0.34027; 22: 0.55773; 23: 0.48258; 24: 0.54231; 25: 0.51041; 26: 0.48923
| f) | 220 kV Control & Potection Panel
|  | Circuit Breaker panel with Auto Reclose | INR Lakhs | 1: 6.28; 2: 0; 3: 5.2334; 4: 6.44; 5: 5.6121; 6: 9.7854; 7: 10.8381; 8: 1.4413; 9: 10.4546; 10: 5.2568; 11: 4.2295; 12: 2.219; 13: 0; 14: 21.48; 15: 8.291; 16: 20.7796; 17: 4.1909; 18: 0; 19: 2.6706; 20: 11.1874; 21: 0; 22: 0; 23: 0; 24: 0; 25: 0; 26: 0
|  | Circuit Breaker panel without Auto Reclose | INR Lakhs | 1: 6.28; 2: 0; 3: 5.2334; 4: 6.44; 5: 5.3588; 6: 8.1719; 7: 9.0377; 8: 1.1384; 9: 9.7268; 10: 2.5944; 11: 2.3345; 12: 1.5022; 13: 0; 14: 15.82; 15: 8.138; 16: 15.2946; 17: 3.1565; 18: 0; 19: 1.9373; 20: 9.6366; 21: 0; 22: 4.34; 23: 0; 24: 0; 25: 0; 26: 0
|  | Line protection panel | INR Lakhs | 1: 24.86; 2: 0; 3: 18.523; 4: 13.58; 5: 13.2971; 6: 18.2784; 7: 15.0292; 8: 9.8161; 9: 17.988; 10: 13.3411; 11: 18.442; 12: 23.5417; 13: 0; 14: 24.54; 15: 20.3833; 16: 23.6787; 17: 29.8266; 18: 0; 19: 15.9535; 20: 18.7508; 21: 13.71; 22: 12.97; 23: 17.14; 24: 0; 25: 0; 26: 0
|  | Bus Bar Protection panel | INR Lakhs | 1: 65.7; 2: 0; 3: 111.98; 4: 50.22; 5: 45.5033; 6: 47.844; 7: 61.22; 8: 0; 9: 73.68; 10: 18.46; 11: 55.9975; 12: 16.94; 13: 0; 14: 86.27; 15: 55.5788; 16: 82.9071; 17: 90.6302; 18: 0; 19: 0; 20: 48.51; 21: 71.14; 22: 74.16; 23: 85.51; 24: 0; 25: 0; 26: 0
| 7 | Foundations
| a) | ICT -315 MVA | INR Lakhs | 1: 15.095
| b) | ICT -S-ph 167 MVA | INR Lakhs | 1: 15.095
| c) | Reactors | INR Lakhs | 1: 10.0633
| d) | 400 kV equipments |  | 1: 0
|  | 420 KV Circuit breakers | INR Lakhs | 1: 1.2579
|  | 420KV Isolators | INR Lakhs | 1: 0.50317
|  | 420 KV Current Transformers | INR Lakhs | 1: 0.10063
|  | 420KV CVT | INR Lakhs | 1: 0.10063
|  | 390KV surge Arrestors | INR Lakhs | 1: 0.050317
|  | Towers , Lattice Type | INR Lakhs | 1: 3.019
|  | Lightning cum Lighting Masts | INR Lakhs | 1: 4.0253
|  | B.P.I. | INR Lakhs | 1: 0.050317
|  | Line( Wave) Traps both for 400 & 220 kV | INR Lakhs | 1: 0.50317
| e) | 220 kV equipments |  | 1: 0
|  | 245 KV Circuit breakers | INR Lakhs | 1: 0.50317
|  | 245 KV Isolators | INR Lakhs | 1: 0.40253
|  | 245 KV Current Transformers | INR Lakhs | 1: 0.10063
|  | 245 KV CVT | INR Lakhs | 1: 0.10063
|  | 216 KV surge Arrestors | INR Lakhs | 1: 0.40253
|  | Towers , Lattice Type | INR Lakhs | 1: 2.5158
|  | BPI | INR Lakhs | 1: 0.40253
| f) | L.T Transformers | INR Lakhs | 1: 0.20127
| 8 | Firewalls for Single Phase ICT & Reactors | INR Lakhs | 1: 1.0063
| 9 | Common Equipments
| a) | Control & Relay panel.
|  | Complete Substation automation system for 400/230kV S/S including hardware and software for remote control station alongthwith associated equipments and Kiosks for the following bays ( bays) as defined in the teechnical specification, Sec-Substaion Automation | INR Lakhs | 1: 0; 2: 0; 3: 0; 4: 0; 5: 0; 6: 0; 7: 0; 8: 0; 9: 0; 10: 0; 11: 0; 12: 0; 13: 0; 14: 0; 15: 0; 16: 0; 17: 0; 18: 0; 19: 0; 20: 0; 21: 0; 22: 0; 23: 0; 24: 0; 25: 0; 26: 0
| b) | LT Switchgear
|  | 800KVA 33/.400 KV Distribution Transformer | INR Lakhs | 1: 7.1552; 2: 19.2959; 3: 10.1907; 4: 14.0913; 5: 13.4179; 6: 14.0394; 7: 10.7038; 8: 9.948; 9: 9.9322; 10: 7.8935; 11: 7.687; 12: 10.164; 13: 0; 14: 8.7545; 15: 11.3102; 16: 8.4269; 17: 6.7545; 18: 0; 19: 14.4783; 20: 10.4965; 21: 13.12; 22: 7.4464; 23: 0; 24: 0; 25: 0; 26: 6.9248
|  | 630KVA, 11/400VKV Distribution Transformer | INR Lakhs | 1: 6.044; 2: 18.4503; 3: 6.7893; 4: 11.6793; 5: 12.9823; 6: 8.4155; 7: 8.2129; 8: 5.4088; 9: 7.1388; 10: 5.5449; 11: 6.2072; 12: 5.0522; 13: 0; 14: 7.3092; 15: 8.1374; 16: 7.4003; 17: 5.8112; 18: 0; 19: 14.4783; 20: 9.144; 21: 10.1038; 22: 6.5332; 23: 12.3392; 24: 9.77; 25: 0; 26: 3.4421
|  | 72.5 kV Isolator with insulators | INR Lakhs | 1: 2.1411; 2: 0; 3: 1.0028; 4: 1.1195; 5: 1.0997; 6: 0.8673; 7: 1.2257; 8: 0; 9: 1.0094; 10: 1.8697; 11: 1.0218; 12: 0; 13: 0; 14: 0; 15: 0; 16: 1.2625; 17: 1.7349; 18: 0; 19: 7.1925; 20: 5.7358; 21: 2.1679; 22: 0.5234; 23: 0; 24: 0; 25: 0; 26: 0
|  | 72.5KV , 1250A, 25KA Circuit Breaker | INR Lakhs | 1: 8.3206; 2: 0; 3: 8.5084; 4: 6.2089; 5: 5.5059; 6: 7.6964; 7: 0; 8: 0; 9: 0; 10: 0; 11: 0; 12: 0; 13: 0; 14: 0; 15: 0; 16: 0; 17: 0; 18: 0; 19: 1.7106; 20: 1.1825; 21: 0; 22: 0; 23: 0; 24: 0; 25: 0; 26: 0
|  | 72.5KV, 25KA, 3 Core Current Transformer 3 Nos | INR Lakhs | 1: 3.8442; 2: 0; 3: 3.415; 4: 2.8044; 5: 0.91639; 6: 0.85374; 22: 22.5998; 23: 0; 24: 0; 25: 0; 26: 0
|  | 72.5KV, 2 Core, 33kV /√3 / 110 V/√3 CVT / PT | INR Lakhs | 1: 3.9028; 2: 0; 3: 2.0801; 4: 2.8044; 5: 0.91639; 6: 0.77244; 22: 21.4595; 23: 0; 24: 0; 25: 0; 26: 0
|  | Relay panel for 800 kVA Transformer on 72.5 kV side |  | 1: 4.37; 2: 0; 3: 4.06; 4: 6.44; 5: 0; 6: 0; 7: 0; 8: 0; 9: 0; 10: 0; 11: 0; 12: 0; 13: 0; 14: 0; 15: 0; 16: 0; 17: 0; 18: 0; 19: 0; 20: 0; 21: 0; 22: 0; 23: 0; 24: 0; 25: 0; 26: 0
|  | 11KV Horn gap Fuse | INR Lakhs | 1: 0.1; 2: 0; 3: 0.16; 4: 0.13; 5: 0.1799; 6: 0.27; 7: 0.17; 8: 0; 9: 0.21; 10: 0.09; 11: 0.12; 12: 0; 13: 0; 14: 0; 15: 0; 16: 0.12; 17: 0.57; 18: 0; 19: 0; 20: 0; 21: 0; 22: 0.42; 23: 0; 24: 0; 25: 0; 26: 0
|  | 11KV Isolator without ES | INR Lakhs | 1: 0.17617; 2: 0; 3: 0.4743; 4: 0.73178; 5: 0.53455; 6: 0.4201; 7: 0; 8: 0; 9: 0.43365; 10: 0.77244; 11: 0.77244; 12: 0; 13: 0; 14: 0; 15: 0; 16: 0.70468; 17: 0.75888; 18: 0; 19: 0.36589; 20: 0.69113; 21: 0; 22: 0; 23: 0; 24: 0; 25: 0; 26: 0
|  | 11KV Surge Arrestor. | INR Lakhs | 1: 0.18; 2: 0; 3: 0.07; 4: 0.11; 5: 0.04498; 6: 0.10216; 7: 0; 8: 0; 9: 0.14; 10: 0; 11: 0.15951; 12: 0; 13: 0; 14: 0; 15: 0; 16: 0.39; 17: 0.31; 18: 0; 19: 0.4; 20: 0.39; 21: 0; 22: 0.48; 23: 0.33; 24: 0.33; 25: 0; 26: 0
|  | 415V Main Switch Board | INR Lakhs | 9.4 | 13.05 | 8.7939 | 11.2887 | 12.8531 | 11.7104 | 15.7583 | 8.7335 | 13.9338 | 12.7533 | 14.9431 | 5.6188 | 0 | 8.7824 | 9.1166 | 8.4847 | 10.683 | 0 | 0.12 | 0.18 | 16.65 | 12.09 | 0 | 0 | 0 | 5.6188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 415V ACDB | INR Lakhs | 1: 9.75; 2: 6.73; 3: 5.7786; 4: 10.9624; 5: 12.9621; 6: 5.1855; 7: 6.9779; 8: 4.2341; 9: 6.3189; 10: 6.3311; 11: 6.7946; 12: 4.3458; 13: 0; 14: 6.3435; 15: 10.2407; 16: 6.1248; 17: 8.3212; 18: 0; 19: 9.8763; 20: 15.1436; 21: 14.52; 22: 11.48; 23: 13.26; 24: 13.26; 25: 0; 26: 4.3458
|  | 415V MLDB | INR Lakhs | 1: 3.08; 2: 2.93; 3: 2.7317; 4: 2.7593; 5: 4.7462; 6: 3.4583; 7: 4.6537; 8: 1.1055; 9: 3.367; 10: 3.7862; 11: 3.62; 12: 2.107; 13: 0; 14: 2.2738; 15: 3.4602; 16: 2.1959; 17: 3.5488; 18: 0; 19: 6.7868; 20: 6.7057; 21: 4.34; 22: 5.02; 23: 7.56; 24: 7.56; 25: 0; 26: 2.107
|  | 415V Emergency LDB | INR Lakhs | 1: 1.23; 2: 0.79; 3: 1.1557; 4: 0.78811; 5: 0.86147; 6: 1.1776; 7: 1.5847; 8: 0.33676; 9: 0.76104; 10: 1.2509; 11: 0.82; 12: 0.55; 13: 0; 14: 0.50748; 15: 0.62298; 16: 0.48998; 17: 1.2849; 18: 0; 19: 2.697; 20: 4.4722; 21: 1.11; 22: 0; 23: 0.65; 24: 0.65; 25: 0; 26: 0.55
|  | 220V DCDB | INR Lakhs | 1: 2.05; 2: 1.49; 3: 0.9666; 4: 3.1627; 5: 2.2541; 6: 1.2954; 7: 4.3368; 8: 3.0651; 9: 1.3837; 10: 1.4378; 11: 1.484; 12: 1.2291; 13: 0; 14: 1.8883; 15: 3.1753; 16: 1.8419; 17: 1.9579; 18: 0; 19: 0.59511; 20: 1.5229; 21: 3.5865; 22: 2.8; 23: 5.1; 24: 5.1; 25: 0; 26: 1.2291
|  | 50V DCDB | INR Lakhs | 1: 1.52; 2: 1.34; 3: 0.91; 4: 3.1574; 5: 2.1624; 6: 1.0599; 7: 1.7432; 8: 1.8598; 9: 1.2453; 10: 1.3659; 11: 1.3363; 12: 1.1589; 13: 0; 14: 1.5224; 15: 2.8047; 16: 1.4699; 17: 1.86; 18: 0; 19: 2.3551; 20: 1.6752; 21: 3.4511; 22: 3.19; 23: 3.19; 24: 3.19; 25: 0; 26: 1.1589
| b) | 220V Battery | INR Lakhs | 1: 6.39; 2: 6.17; 3: 5.6951; 4: 4.5744; 5: 5.1121; 6: 5.4667; 7: 6.378; 8: 5.2205; 9: 5.5809; 10: 4.5743; 11: 6.3368; 12: 5.22; 13: 0; 14: 6.59; 15: 7.7077; 16: 6.3608; 17: 9.8509; 18: 0; 19: 1.6972; 20: 1.3706; 21: 17.43; 22: 10.41; 23: 7.5021; 24: 7.5021; 25: 0; 26: 5.22
| c) | 50V Battery | INR Lakhs | 1: 1.94; 2: 1.69; 3: 1.414; 4: 1.2147; 5: 1.4523; 6: 1.6566; 7: 1.9327; 8: 1.2157; 9: 1.7588; 10: 1.6634; 11: 1.8731; 12: 1.1913; 13: 0; 14: 1.79; 15: 1.7128; 16: 1.6469; 17: 2.9859; 18: 0; 19: 5.37; 20: 5.4814; 21: 3.8; 22: 7.92; 23: 2.8179; 24: 2.8179; 25: 0; 26: 1.1913
| d) | Battery Charger for 220V Battery | INR Lakhs | 1: 1.5; 2: 2.93; 3: 3.5597; 4: 2.3465; 5: 2.8484; 6: 1.1982; 7: 1.6358; 8: 1.7801; 9: 2.4599; 10: 1.5646; 11: 1.5206; 12: 2.0811; 13: 0; 14: 1.7663; 15: 2.9513; 16: 1.7059; 17: 1.7499; 18: 0; 19: 1.53; 20: 1.625; 21: 3.7; 22: 10.38; 23: 3.6704; 24: 3.6704; 25: 0; 26: 2.0811
| e) | Battery Charger for 50V Battery | INR Lakhs | 1: 1.06; 2: 2.26; 3: 2.6608; 4: 1.7944; 5: 1.835; 6: 1.0955; 7: 1.4956; 8: 1.1337; 9: 1.5887; 10: 1.1043; 11: 1.2886; 12: 1.1775; 13: 0; 14: 1.5224; 15: 1.7439; 16: 1.4699; 17: 1.2971; 18: 0; 19: 2.1457; 20: 1.5177; 21: 1.79; 22: 3.54; 23: 2.8596; 24: 2.8596; 25: 0; 26: 1.1775
| f) | DG Set-250KVA with control panel | INR Lakhs | 1: 13.39; 2: 17.63; 3: 19.62; 4: 22.21; 5: 24.7511; 6: 15.05; 7: 19.35; 8: 10.81; 9: 23.574; 10: 12.09; 11: 13.46; 12: 13; 13: 0; 14: 18.78; 15: 18.7138; 16: 18.3293; 17: 14.68; 18: 0; 19: 1.4955; 20: 1.3154; 21: 17.61; 22: 21.18; 23: 0; 24: 0; 25: 0; 26: 13
| g) | High Wall Type Split AC unit of 2TR Capacity | INR Lakhs | 1: 0.36; 2: 0.44003; 3: 0.3; 4: 0.32; 5: 0.37177; 6: 0.41; 7: 0.49; 8: 0; 9: 0.29232; 10: 0; 11: 0.25; 12: 0.3; 13: 0; 14: 0; 15: 0; 16: 0.48; 17: 0.31; 18: 0; 19: 20.06; 20: 18.62; 21: 0; 22: 0; 23: 0; 24: 0; 25: 0; 26: 0.3
| h) | Illumination(Indoor and Outdoor) | INR Lakhs | 1: 0; 2: 0; 3: 0; 4: 0; 5: 0; 6: 0; 7: 0; 8: 0; 9: 0; 10: 0; 11: 0; 12: 0; 13: 0; 14: 0; 15: 0; 16: 0; 17: 0; 18: 0; 19: 0.38; 20: 0.39; 21: 0; 22: 0; 23: 0; 24: 0; 25: 0; 26: 0
| 10 | PLCC equipments on 400 kV side (Both for 400 & 220 kV) | INR Lakhs | 1: 0; 2: 0; 3: 0; 4: 0; 5: 0; 6: 0; 7: 0; 8: 0; 9: 0; 10: 0; 11: 0; 12: 0; 13: 0; 14: 0; 15: 0; 16: 0; 17: 0; 18: 0; 19: 0; 20: 0; 21: 0; 22: 0; 23: 0; 24: 0; 25: 0; 26: 0
| 11 | Mandatory Spares | INR Lakhs | 1: 0; 2: 0; 3: 0; 4: 0; 5: 0; 6: 0; 7: 0; 8: 0; 9: 0; 10: 0; 11: 0; 12: 0; 13: 0; 14: 0; 15: 0; 16: 0; 17: 0; 18: 0; 19: 0; 20: 0; 21: 0; 22: 0; 23: 0; 24: 0; 25: 0; 26: 0
| 12 | Steel Structures - Unit MT
| a) | Lattice Type | INR Lakhs | 1: 0.68144
| b) | Tubular support structures | INR Lakhs | 1: 0.90858
| 13 | Earth mat- 40 mm rods - Per kM | INR Lakhs | 1: 5.8481
| 14 | Bus Bar Materials
| a) | 400 kV Switchyard | INR Lakhs | 1: 175.7157
Moose ACSR
Twin disc Ins. string with Tension Hardware fr Twin Moose
Twin disc Ins. string with Suspension Hardware fr Twin Moose
400KV BPI
Tee Clamp for Twin Moose to 4" IPS Al. Tube
Tee Clamp for Twin Moose to Twin Moose ACSR
PG Clamps
Spacer to Twin Moose ACSR
Ground wire and accessories
| b) | 220 kV Switchyard | INR Lakhs | 1: 197.6802
Quad disc Ins. string with Tension Hardware fr Quad Moose
Twin disc Ins. string with Suspension Hardware fr Quad Moose
Twin disc Ins. string with Tension Hardware fr Twin Moose
Twin disc Ins. string with Suspension Hardware fr Twin Moose
220KV BPI
4" IPS Al. Tube
Moose ACSR
Tee Clamp for Quad Moose to Twin Moose ACSR
Tee Clamp for Twin Moose to Twin Moose ACSR
Tee Clamp for Twin Moose to 4" IPS Al. Tube
Spacer to Quad Moose ACSR
Spacer to Twin Moose ACSR
PG Clamps
Ground wire and accessories
| 15 | Fire fighting Equipment including one 315 MVA Transformer. | INR Lakhs | 1: 75.4751
| 16 | Power Cables -- Cost per kM | INR Lakhs | 1: 1.223
| 17 | Control cables --- Cost per kM | INR Lakhs | 1: 1.0192
| 18 | Land devolopment & Civil engineering works
| a) | Soil Investigation (lump Sum) | INR Lakhs | 1: 2.2285
| b) | Intial Civil Engineering Works like Levelling,Retaining walls, Appoach Road, Peripheral Fencing etc. (lump Sum) | INR Lakhs | 1: 70.4434
| c) | Ant weed treatment & Site Surfing Cost per Meter | INR Lakhs | 1: 0.00055921
| d) | Road work (Cost per Meter) | INR Lakhs | 1: 0.020294
| e) | Storm water drain, Road culverts drain crossing, cable trench crossing | INR Lakhs | 1: 0.015698
| f) | Switch yard fencing | INR Lakhs | 1: 0.00080224
| g) | DG room & Fire fighting Room (FFPH) | INR Lakhs | 1: 56.3547
| h) | Control room with cable vaults | INR Lakhs | 1: 100.6334
| j) | Cable ducts | INR Lakhs | 1: 90.5701
| j) | Providing water supply including drinking water & water for fire fighting system and sewage system | INR Lakhs | 1: 5.5711
| k) | Parking sheds,Rain water Harvesting systems & land scaping etc. | INR Lakhs | 1: 30.19
| 19 | Erection charges
| a) | Common equipments
|  | Auxiliary Transformers,LT Switchgear, AC & DC Panels.72.5 kV ,33kV & 11 kV equipments etc. | INR Lakhs | 1: 2.2285
|  | Station D.C Batteries 220 V, 500 AH | INR Lakhs | 1: 0.27811
|  | Station D.C Batteries 50 V, 500 AH | INR Lakhs | 1: 0.11588
|  | Battery Charger System 220 V, 70A / 50 A Float cum Boost | INR Lakhs | 1: 0.22285
|  | Battery Charger System 50 V, 70 A / 50 A Float cum Boost | INR Lakhs | 1: 0.16713
|  | Common equipment pertaining to C&R system.( Automation) | INR Lakhs | 1: 7.7996
|  | Power cables | INR Lakhs | 1: 4.4569
|  | Control cables | INR Lakhs | 1: 6.6854
|  | Earth mat 40 mm Rods ( Main Earth Mat) | INR Lakhs | 1: 16.7134
|  | Diesel Generator set with AMF panel 250 kVA | INR Lakhs | 1: 0.66854
|  | Air Conditioning and Ventilation | INR Lakhs | 1: 1.0028
|  | Fire Fighting System | INR Lakhs | 1: 8.9138
|  | Lightning & lightnening masts | INR Lakhs | 1: 1.0028
|  | Illumination System - Indoor & outdoor | INR Lakhs | 1: 11.1423
| b) | ICTs ( Power Transformers) |  | 1: 0
|  | I.C.T 315 MVA, 3Phase, 400/220/33 KV class | INR Lakhs | 1: 6.6854
|  | I.C.T 167 MVA, S-Phase, 400/220 kV ( Single Phase 167 MVA Units) | INR Lakhs | 1: 6.6854
| c) | Shunt & Bus Reactors 400 kV | INR Lakhs | 1: 4.4569
| d) | 400 kV equipments |  | 1: 0
|  | 420 KV Circuit breakers | INR Lakhs | 1: 0.33427
|  | 420KV Isolators | INR Lakhs | 1: 0.22285
|  | 420 KV Current Transformers | INR Lakhs | 1: 0.066854
|  | 420KV CVT | INR Lakhs | 1: 0.066854
|  | 390KV surge Arrestors | INR Lakhs | 1: 0.033427
|  | Towers , Beams Lattice Type | INR Lakhs | 1: 7.0196
|  | Tubular type pipe structures | INR Lakhs | 1: 2.2285
|  | Bus Bars formation etc. | INR Lakhs | 1: 16.7134
| e) | Control & Protection panels |  | 1: 0
|  | 400KV CB relay Panel | INR Lakhs | 1: 0.33427
|  | 400KV Line Protection Panel | INR Lakhs | 1: 1.0028
|  | 400-220/33KV Transformer Protection Panel | INR Lakhs | 1: 0.60895
|  | 400KV Reactor Protection Panel | INR Lakhs | 1: 0.10648
|  | Duplicate Bus Bar Protection Panel - 400KV | INR Lakhs | 1: 1.781
|  | PLCC Equipments (Both for 400 kV & 220 kV) | INR Lakhs | 1: 1.3928
| f) | 220 kV Equipments |  | 1: 0
|  | 245 KV Circuit breakers | INR Lakhs | 1: 0.22285
|  | 245 KV Isolators | INR Lakhs | 1: 0.16713
|  | 245 KV Current Transformers | INR Lakhs | 1: 0.055711
|  | 245 KV CVT | INR Lakhs | 1: 0.055711
|  | 216 KV surge Arrestors | INR Lakhs | 1: 0.033427
| h) | 220 kV Towers & beams | INR Lakhs | 1: 6.6854
| i) | 220 tubular pipe structures | INR Lakhs | 1: 3.3427
| j) | 220 kV Bus Bars formation etc | INR Lakhs | 1: 17.8277
| k) | Control & Protection panels |  | 1: 0
|  | Circuit breaker relay panel With Auto reclosure | INR Lakhs | 1: 0.27856
|  | Line protection panel | INR Lakhs | 1: 0.73539
|  | Single Bus Bar protection panel | INR Lakhs | 1: 2.2285

## Average Rates
CERC
Capital Cost Benchmarking
Average Rates
Name of the Utility
Name of sub-station
Reference P.O. No.
Month and Year of Commissioning
| S.No. | Name of the Component | Unit | Final Rates | Average Rate Excluding Taxes and Duties
| 1 | Power Transformer
| a) | ICT 400/√3/220 √3/ 33KV,167 MVA, single phase autotransformer including Insulating Oil Frieght & Insurance | INR Lakhs | 488.9265 | 488.9265
| b) | I.C.T 315 MVA, 3 Phase, 400/220/33 KV including including Insulating Oil Frieght & Insurance | INR Lakhs | 869.9688 | 869.9688
| c) | ICT 400/√3/220 √3/ 33KV,105 MVA, single phase autotransformer including Insulating Oil Frieght & Insurance | INR Lakhs | 389.3257 | 389.3257
| d) | I.C.T 250 MVA, 3 Phase, 400/220/33 KV including including Insulating Oil Frieght & Insurance | INR Lakhs | 786.5113 | 786.5113
0
| 2 | Shunt Reactor |  | 0
| a) | 420KV, 125 MVAR, 3-Phase Shunt Reactor | INR Lakhs | 396.3704 | 396.3704
| b) | 420KV, 80 MVAR, 3-Phase Shunt Reactor | INR Lakhs | 378.1723 | 378.1723
| c) | 420KV, 63/50 MVAR, 3-Phase Shunt Reactor | INR Lakhs | 340.5353 | 340.5353
| d) | NGR with oil, for above 400 kV Shunt Reactor | INR Lakhs | 24.3159 | 24.3159
| e) | Surge Arrestors 120 kV for NGR | INR Lakhs | 1.5995 | 1.5995
| f) | Spares for NGR &120KV SA | INR Lakhs | 0 | 0
| 3 | Bus Reactor
| a) | 125 MVAR 400 kV | INR Lakhs
| b) | 80 MVAR 400 kV | INR Lakhs
| c) | 63 / 50 MVAR 400 kV | INR Lakhs
| d) | 50 MVAR | INR Lakhs
| e) | Oil for shunt Reactor | INR Lakhs
| f) | Spares for Bus Reactor | INR Lakhs
| 4 | 420 kV Equipments
| a) | 420 kV Breakers with CR | INR Lakhs | 46.2398 | 46.2398
| b) | 420 kVBreakers without CR | INR Lakhs | 42.403 | 42.403
| c) | 420 kV CTs 2000A, 40KA, 5-Core, | INR Lakhs | 7.5111 | 7.5111
| d) | 420 kv CVT 4400 PF | INR Lakhs | 5.4346 | 5.4346
| e) | 420 kv CVT 8800 PF | INR Lakhs | 6.8105 | 6.8105
| f) | 420 KV,2000 A,40 kA Isolators 3-Phase with one E/S (3 Phase) with insulators | INR Lakhs | 9.4556 | 9.4556
| g) | 420 KV,2000A,40 kA Isolators 3-Phase with two E/S with insulators | INR Lakhs | 10.8353 | 10.8353
| h) | 420 KV,2000A,40 kA Isolators one Phase with one E/S | INR Lakhs | 2.2966 | 2.2966
| j) | Surge Arrestors 390 kV | INR Lakhs | 1.8754 | 1.8754
| 5 | 400 kV Control and Protection Panel
| a) | Circuit Breaker panel with Auto Reclose | INR Lakhs | 8.3151 | 8.3151
| b) | Circuit Breaker panel without Auto Reclose | INR Lakhs | 6.607 | 6.607
| c) | Line protection panel | INR Lakhs | 19.6415 | 19.6415
| d) | Transformer protection panel(both HV and MV) | INR Lakhs | 16.1881 | 16.1881
| e) | Reactor protection panel | INR Lakhs | 12.2936 | 12.2936
| f) | Bus Bar Protection Panel | INR Lakhs | 107.1515 | 107.1515
| 6 | 245 kV Equipment
| a) | Circuit Breakers 245 kV
|  | 1600 A, 40 kA | INR Lakhs | 17.3378 | 17.3378
|  | 2500 A, 40 kA | INR Lakhs | 17.9053 | 17.9053
| b) | Current Transformers 245 kV |  | 0
|  | 1600 A, 40 kA , 5 core, with 120% extended current | INR Lakhs | 3.7043 | 3.7043
|  | 1600 A, 40 kA, 5 core, with 150% extended current | INR Lakhs | 3.9553 | 3.9553
| c) | Capacitive Voltage Transformer 245 kV |  | 0
|  | 8800 pf, S- Ph, with 3 secondaries | INR Lakhs | 3.34 | 3.34
|  | 4400 pf, S- Ph with 3 secondaries | INR Lakhs | 3.3359 | 3.3359
| d) | Isolators 245 kV |  | 0
|  | 1600A, 40 kA, DB Type with two E/S | INR Lakhs | 4.5691 | 4.5691
|  | 1600A, 40 kA, DB Type with one E/S | INR Lakhs | 3.8603 | 3.8603
|  | 1600A, 40 kA, DB, Tandem Type without E/S | INR Lakhs | 3.4448 | 3.4448
|  | 2500A, 40 KA, DB Type with Two E/S | INR Lakhs | 4.8228 | 4.8228
|  | 1600A, 40 kA with one E/S S-phase | INR Lakhs | 1.7311 | 1.7311
|  | 1600A, 40 kA without E/S S phase | INR Lakhs | 1.1722 | 1.1722
| e) | 216 kV Surge Arrestors | INR Lakhs | 0.74356 | 0.74356
| f) | 220 kV Control & Potection Panel |  | 0
|  | Circuit Breaker panel with Auto Reclose | INR Lakhs | 8.0229 | 8.0229
|  | Circuit Breaker panel without Auto Reclose | INR Lakhs | 6.4523 | 6.4523
|  | Line protection panel | INR Lakhs | 18.1825 | 18.1825
|  | Bus Bar Protection panel | INR Lakhs | 63.4584 | 63.4584
0
| 7 | Foundations |  | 0
| a) | ICT -315 MVA | INR Lakhs | 15.095 | 15.095
| b) | ICT -S-ph 167 MVA | INR Lakhs | 15.095 | 15.095
| c) | Reactors | INR Lakhs | 10.0633 | 10.0633
| d) | 400 kV equipments
|  | 420 KV Circuit breakers | INR Lakhs | 1.2579 | 1.2579
|  | 420KV Isolators | INR Lakhs | 0.50317 | 0.50317
|  | 420 KV Current Transformers | INR Lakhs | 0.10063 | 0.10063
|  | 420KV CVT | INR Lakhs | 0.10063 | 0.10063
|  | 390KV surge Arrestors | INR Lakhs | 0.050317 | 0.050317
|  | Towers , Lattice Type | INR Lakhs | 3.019 | 3.019
|  | Lightning cum Lighting Masts | INR Lakhs | 4.0253 | 4.0253
|  | B.P.I. | INR Lakhs | 0.050317 | 0.050317
|  | Line( Wave) Traps both for 400 & 220 kV | INR Lakhs | 0.50317 | 0.50317
| e) | 220 kV equipments
|  | 245 KV Circuit breakers | INR Lakhs | 0.50317 | 0.50317
|  | 245 KV Isolators | INR Lakhs | 0.40253 | 0.40253
|  | 245 KV Current Transformers | INR Lakhs | 0.10063 | 0.10063
|  | 245 KV CVT | INR Lakhs | 0.10063 | 0.10063
|  | 216 KV surge Arrestors | INR Lakhs | 0.40253 | 0.40253
|  | Towers , Lattice Type | INR Lakhs | 2.5158 | 2.5158
|  | BPI | INR Lakhs | 0.40253 | 0.40253
| f) | L.T Transformers | INR Lakhs | 0.20127 | 0.20127
| 8 | Firewalls for Single Phase ICT & Reactors | INR Lakhs | 1.0063 | 1.0063
0
| 9 | Common Equipments |  | 0
| a) | Control & Relay panel. |  | 0
|  | Complete Substation automation system for 400/230kV S/S including hardware and software for remote control station alongthwith associated equipments and Kiosks for the following bays ( bays) as defined in the teechnical specification, Sec-Substaion Automation | INR Lakhs | 250 | 250
| b) | LT Switchgear | INR Lakhs | 69.3932 | 69.3932
|  | 800KVA 33/.400 KV Distribution Transformer | INR Lakhs | 10.5824 | 10.5824
|  | 630KVA, 11/400VKV Distribution Transformer | INR Lakhs | 8.5389 | 8.5389
|  | 72.5 kV Isolator with insulators | INR Lakhs | 1.9983 | 1.9983
|  | 72.5KV , 1250A, 25KA Circuit Breaker | INR Lakhs | 5.5905 | 5.5905
|  | 72.5KV, 25KA, 3 Core Current Transformer 3 Nos | INR Lakhs | 5.7389 | 5.7389
|  | 72.5KV, 2 Core, 33kV /√3 / 110 V/√3 CVT / PT | INR Lakhs | 5.3226 | 5.3226
|  | Relay panel for 800 kVA Transformer on 72.5 kV side | INR Lakhs | 4.9567 | 4.9567
|  | 11KV Horn gap Fuse | INR Lakhs | 0.20677 | 0.20677
|  | 11KV Isolator without ES | INR Lakhs | 0.39114 | 0.39114
|  | 11KV Surge Arrestor. | INR Lakhs | 0.24443 | 0.24443
|  | 415V Main Switch Board | INR Lakhs | 10.0268 | 10.0268
|  | 415V ACDB | INR Lakhs | 8.6646 | 8.6646
|  | 415V MLDB | INR Lakhs | 3.8001 | 3.8001
|  | 415V Emergency LDB | INR Lakhs | 1.0819 | 1.0819
|  | 220V DCDB | INR Lakhs | 2.2492 | 2.2492
|  | 50V DCDB | INR Lakhs | 1.895 | 1.895
| b) | 220V Battery | INR Lakhs | 6.4504 | 6.4504
| c) | 50V Battery | INR Lakhs | 2.4136 | 2.4136
| d) | Battery Charger for 220V Battery | INR Lakhs | 2.6198 | 2.6198
| e) | Battery Charger for 50V Battery | INR Lakhs | 1.7573 | 1.7573
| f) | DG Set-250KVA with control panel | INR Lakhs | 20.2349 | 20.2349
| g) | High Wall Type Split AC unit of 2TR Capacity | INR Lakhs | 0.36 | 0.36
| h) | Illumination(Indoor and Outdoor) | INR Lakhs | 55 | 55
0
| 10 | PLCC equipments on 400 kV side (Both for 400 & 220 kV) | INR Lakhs | 76 | 76
0
| 11 | Mandatory Spares | INR Lakhs | 175 | 175
0
| 12 | Steel Structures - Unit MT |  | 0
| a) | Lattice Type | INR Lakhs | 0.68144 | 0.68144
| b) | Tubular support structures | INR Lakhs | 0.90858 | 0.90858
0
| 13 | Earth mat- 40 mm rods - Per kM | INR Lakhs | 5.8481 | 5.8481
0
| 14 | Bus Bar Materials |  | 0
| a) | 400 kV Switchyard | INR Lakhs | 175.7157 | 175.7157
|  | A |  | 0
|  | Moose ACSR |  | 0
|  | Twin disc Ins. string with Tension Hardware fr Twin Moose |  | 0
|  | Twin disc Ins. string with Suspension Hardware fr Twin Moose |  | 0
|  | 400KV BPI |  | 0
|  | Tee Clamp for Twin Moose to 4" IPS Al. Tube |  | 0
|  | Tee Clamp for Twin Moose to Twin Moose ACSR |  | 0
|  | PG Clamps |  | 0
|  | Spacer to Twin Moose ACSR |  | 0
|  | Ground wire and accessories |  | 0
| b) | 220 kV Switchyard | INR Lakhs | 197.6802 | 197.6802
|  | Quad disc Ins. string with Tension Hardware fr Quad Moose |  | 0
|  | Twin disc Ins. string with Suspension Hardware fr Quad Moose |  | 0
|  | Twin disc Ins. string with Tension Hardware fr Twin Moose |  | 0
|  | Twin disc Ins. string with Suspension Hardware fr Twin Moose |  | 0
|  | 220KV BPI |  | 0
|  | 4" IPS Al. Tube |  | 0
|  | Moose ACSR |  | 0
|  | Tee Clamp for Quad Moose to Twin Moose ACSR |  | 0
|  | Tee Clamp for Twin Moose to Twin Moose ACSR |  | 0
|  | Tee Clamp for Twin Moose to 4" IPS Al. Tube |  | 0
|  | Spacer to Quad Moose ACSR |  | 0
|  | Spacer to Twin Moose ACSR |  | 0
|  | PG Clamps |  | 0
|  | Ground wire and accessories |  | 0
0
| 15 | Fire fighting Equipment including one 315 MVA Transformer. | INR Lakhs | 75 | 75
0
| 16 | Power Cables -- Cost per kM | INR Lakhs | 1.223 | 1.223
0
| 17 | Control cables --- Cost per kM | INR Lakhs | 1.0192 | 1.0192
0
| 18 | Land devolopment & Civil engineering works |  | 0
| a) | Soil Investigation (lump Sum) | INR Lakhs | 2.2285 | 2.2285
| b) | Intial Civil Engineering Works like Levelling,Retaining walls, Appoach Road, Peripheral Fencing etc. (lump Sum) | INR Lakhs | 70.4434 | 70.4434
| c) | Ant weed treatment & Site Surfing Cost per Meter | INR Lakhs | 0.00055921 | 0.00055921
| d) | Road work (Cost per Meter) | INR Lakhs | 0.020294 | 0.020294
| e) | Storm water drain, Road culverts drain crossing, cable trench crossing | INR Lakhs | 0.015698 | 0.015698
| f) | Switch yard fencing | INR Lakhs | 0.00080224 | 0.00080224
| g) | DG room & Fire fighting Room (FFPH) | INR Lakhs | 56.3547 | 56.3547
| h) | Control room with cable vaults | INR Lakhs | 100.6334 | 100.6334
| j) | Cable ducts | INR Lakhs | 90.5701 | 90.5701
| j) | Providing water supply including drinking water & water for fire fighting system and sewage system | INR Lakhs | 5.5711 | 5.5711
| k) | Parking sheds,Rain water Harvesting systems & land scaping etc. | INR Lakhs | 30.19 | 30.19
0
| 19 | Erection charges |  | 0
| a) | Common equipments |  | 0
|  | Auxiliary Transformers,LT Switchgear, AC & DC Panels.72.5 kV ,33kV & 11 kV equipments etc. | INR Lakhs | 2.2285 | 2.2285
|  | Station D.C Batteries 220 V, 500 AH | INR Lakhs | 0.27811 | 0.27811
|  | Station D.C Batteries 50 V, 500 AH | INR Lakhs | 0.11588 | 0.11588
|  | Battery Charger System 220 V, 70A / 50 A Float cum Boost | INR Lakhs | 0.22285 | 0.22285
|  | Battery Charger System 50 V, 70 A / 50 A Float cum Boost | INR Lakhs | 0.16713 | 0.16713
|  | Common equipment pertaining to C&R system.( Automation) | INR Lakhs | 7.7996 | 7.7996
|  | Power cables | INR Lakhs | 4.4569 | 4.4569
|  | Control cables | INR Lakhs | 6.6854 | 6.6854
|  | Earth mat 40 mm Rods ( Main Earth Mat) | INR Lakhs | 16.7134 | 16.7134
|  | Diesel Generator set with AMF panel 250 kVA | INR Lakhs | 0.66854 | 0.66854
|  | Air Conditioning and Ventilation | INR Lakhs | 1.0028 | 1.0028
|  | Fire Fighting System | INR Lakhs | 8.9138 | 8.9138
|  | Lightning & lightnening masts | INR Lakhs | 1.0028 | 1.0028
|  | Illumination System - Indoor & outdoor | INR Lakhs | 11.1423 | 11.1423
| b) | ICTs ( Power Transformers) |  | 0
|  | I.C.T 315 MVA, 3Phase, 400/220/33 KV class | INR Lakhs | 6.6854 | 6.6854
|  | I.C.T 167 MVA, S-Phase, 400/220 kV ( Single Phase 167 MVA Units) | INR Lakhs | 6.6854 | 6.6854
| c) | Shunt & Bus Reactors 400 kV | INR Lakhs | 4.4569 | 4.4569
| d) | 400 kV equipments |  | 0 | 0
|  | 420 KV Circuit breakers | INR Lakhs | 0.33427 | 0.33427
|  | 420KV Isolators | INR Lakhs | 0.22285 | 0.22285
|  | 420 KV Current Transformers | INR Lakhs | 0.066854 | 0.066854
|  | 420KV CVT | INR Lakhs | 0.066854 | 0.066854
|  | 390KV surge Arrestors | INR Lakhs | 0.033427 | 0.033427
|  | Towers , Beams Lattice Type | INR Lakhs | 7.0196 | 7.0196
|  | Tubular type pipe structures | INR Lakhs | 2.2285 | 2.2285
|  | Bus Bars formation etc. | INR Lakhs | 16.7134 | 16.7134
| e) | Control & Protection panels |  | 0 | 0
|  | 400KV CB relay Panel | INR Lakhs | 0.33427 | 0.33427
|  | 400KV Line Protection Panel | INR Lakhs | 1.0028 | 1.0028
|  | 400-220/33KV Transformer Protection Panel | INR Lakhs | 0.60895 | 0.60895
|  | 400KV Reactor Protection Panel | INR Lakhs | 0.10648 | 0.10648
|  | Duplicate Bus Bar Protection Panel - 400KV | INR Lakhs | 1.781 | 1.781
|  | PLCC Equipments (Both for 400 kV & 220 kV) | INR Lakhs | 1.3928 | 1.3928
| f) | 220 kV Equipments |  | 0 | 0
|  | 245 KV Circuit breakers | INR Lakhs | 0.22285 | 0.22285
|  | 245 KV Isolators | INR Lakhs | 0.16713 | 0.16713
|  | 245 KV Current Transformers | INR Lakhs | 0.055711 | 0.055711
|  | 245 KV CVT | INR Lakhs | 0.055711 | 0.055711
|  | 216 KV surge Arrestors | INR Lakhs | 0.033427 | 0.033427
| h) | 220 kV Towers & beams | INR Lakhs | 6.6854 | 6.6854
| i) | 220 tubular pipe structures | INR Lakhs | 3.3427 | 3.3427
| j) | 220 kV Bus Bars formation etc | INR Lakhs | 17.8277 | 17.8277
| k) | Control & Protection panels |  | 0 | 0
|  | Circuit breaker relay panel With Auto reclosure | INR Lakhs | 0.27856 | 0.27856
|  | Line protection panel | INR Lakhs | 0.73539 | 0.73539
|  | Single Bus Bar protection panel | INR Lakhs | 2.2285 | 2.2285

## Alternates & Combinations
CERC
Capital Cost Benchmarking
BOQ & Cost for 400 / 220 KV Sub Station of various combinations of Bays,ICTs,Shunt & Bus Reactors for new 400/220 kV Sub-Stations (Green field stations)
| S.No | Description | Unit | Rate | ALT - 1 |  | ALT - 2 |  | ALT - 3 |  | ALT - 4 |  | ALT - 5 |  | ALT - 6 |  | ALT - 7 |  | ALT - 8 |  | ALT - 9 |  | ALT - 10 |  | ALT - 11 |  | ALT - 12 |  | ALT - 13 |  | ALT - 14 |  | ALT - 15 |  | ALT - 16 |  | ALT - 17 |  | ALT - 18 |  | ALT - 19 |  | ALT - 20 |  | 400 kV Line Bay with Shunt Reactor |  | 400kV Line Bay |  | 220KV Line Bay |  | 1X315 MVA ICT with 400KV & 220KV Bays |  | Addition of Shunt Reactor to 400KV Line Bay |  | 400 kV Bus Reactor Bay
| 1 | Common General Works |  |  | Quantity | Amount | Quantity | Amount | Quantity | Amount | Quantity | Amount | Quantity | Amount | Quantity | Amount | Quantity | Amount | Quantity | Amount | Quantity | Amount | Quantity | Amount | Quantity | Amount | Quantity | Amount | Quantity | Amount | Quantity | Amount | Quantity | Amount | Quantity | Amount | Quantity | Amount | Quantity | Amount | Quantity | Amount |  |  | Quantity | Amount | Quantity | Amount | Quantity | Amount | Quantity | Amount | Quantity | Amount | Quantity | Amount
| 1-A | Land devolopment & Civil engineering works
| a) | Soil Investigation (lump Sum) | Lump Sum | 2.2285 | 1 | 2.2285 | 1 | 2.2285 | 1 | 2.2285 | 1 | 2.2285 | 1 | 2.2285 | 1 | 2.2285 | 1 | 2.2285 | 1 | 2.2285 | 1 | 2.2285 | 1 | 2.2285 | 1 | 2.2285 | 1 | 2.2285 | 1 | 2.2285 | 1 | 2.2285 | 1 | 2.2285 | 1 | 2.2285 | 1 | 2.2285 | 1 | 2.2285 | 1 | 2.2285 | 1 | 2.2285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) | Intial Civil Engineering Works like Levelling,Retaining walls,Appoch Road,Peripheral Fencing etc (lump Sum) | Lump Sum | 70.4434 | 1 | 70.4434 | 1 | 70.4434 | 1 | 70.4434 | 1 | 70.4434 | 1 | 70.4434 | 1 | 70.4434 | 1 | 70.4434 | 1 | 70.4434 | 1 | 70.4434 | 1 | 70.4434 | 1 | 70.4434 | 1 | 70.4434 | 1 | 70.4434 | 1 | 70.4434 | 1 | 70.4434 | 1 | 70.4434 | 1 | 70.4434 | 1 | 70.4434 | 1 | 70.4434 | 1 | 70.4434 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| c) | Ant weed treatment & Site Surfing Cost per Meter | Sq mt | 0.00055921 | 130600 | 73.0327 | 130600 | 73.0327 | 109000 | 60.9538 | 125200 | 70.0129 | 103600 | 57.934 | 103600 | 57.934 | 153000 | 85.5589 | 176400 | 98.6444 | 238800 | 133.5391 | 173800 | 97.1905 | 125200 | 70.0129 | 114400 | 63.9735 | 114400 | 63.9735 | 173800 | 97.1905 | 130600 | 73.0327 | 103600 | 57.934 | 114200 | 63.8616 | 238800 | 133.5391 | 100980 | 56.4689 | 100980 | 56.4689 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| e) | Road work (Cost per Meter) | Metre | 0.020294 | 2900 | 58.852 | 2900 | 58.852 | 2900 | 58.852 | 2900 | 58.852 | 1700 | 34.4995 | 1700 | 34.4995 | 3360 | 68.1872 | 3500 | 71.0283 | 3750 | 76.1018 | 3360 | 68.1872 | 1700 | 34.4995 | 1700 | 34.4995 | 1700 | 34.4995 | 3360 | 68.1872 | 2900 | 58.852 | 1700 | 34.4995 | 1700 | 34.4995 | 6000 | 121.7628 | 2217.6 | 45.0035 | 1663.2 | 33.7527 | 30 | 0.60881 | 30 | 0.60881 | 20 | 0.40588 | 90 | 1.8264 | 0 | 0 | 30 | 0.60881
| d) | Storm water drain, Road culverts drain crossing, cable trench crossing | Metre | 0.015698 | 2120 | 33.2795 | 2120 | 33.2795 | 2120 | 33.2795 | 2120 | 33.2795 | 2000 | 31.3957 | 2000 | 31.3957 | 2520 | 39.5586 | 2720 | 42.6982 | 4487.449 | 70.4434 | 2520 | 39.5586 | 2000 | 31.3957 | 2000 | 31.3957 | 2000 | 31.3957 | 2520 | 39.5586 | 2120 | 33.2795 | 2000 | 31.3957 | 2000 | 31.3957 | 7000 | 109.8851 | 1663.2 | 26.1087 | 1247.4 | 19.5815 | 30 | 0.47094 | 30 | 0.47094 | 20 | 0.31396 | 90 | 1.4128 | 0 | 0 | 30 | 0.47094
| e) | Switch yard fencing | Metre | 0.00080224 | 2052 | 1.6462 | 2052 | 1.6462 | 2052 | 1.6462 | 1944 | 1.5596 | 1836 | 1.4729 | 1836 | 1.4729 | 2164 | 1.7361 | 2632 | 2.1115 | 2944 | 2.3618 | 2268 | 1.8195 | 1944 | 1.5596 | 1890 | 1.5162 | 1890 | 1.5162 | 2268 | 1.8195 | 2052 | 1.6462 | 1836 | 1.4729 | 1890 | 1.5162 | 2496 | 2.0024 | 1428.24 | 1.1458 | 1428 | 1.1456 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| f) | DG room & Fire fighting Room (FFPH) | No | 56.3547 | 1 | 56.3547 | 1 | 56.3547 | 1 | 56.3547 | 1 | 56.3547 | 1 | 56.3547 | 1 | 56.3547 | 1 | 56.3547 | 1 | 56.3547 | 1 | 56.3547 | 1 | 56.3547 | 1 | 56.3547 | 1 | 56.3547 | 1 | 56.3547 | 1 | 56.3547 | 1 | 56.3547 | 1 | 56.3547 | 1 | 56.3547 | 1 | 56.3547 | 1 | 56.3547 | 1 | 56.3547 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| g) | Control room with cable vaults | No | 100.6334 | 1 | 100.6334 | 1 | 100.6334 | 1 | 100.6334 | 1 | 100.6334 | 1 | 100.6334 | 1 | 100.6334 | 1 | 100.6334 | 1 | 100.6334 | 1 | 100.6334 | 1 | 100.6334 | 1 | 100.6334 | 1 | 100.6334 | 1 | 100.6334 | 1 | 100.6334 | 1 | 100.6334 | 1 | 100.6334 | 1 | 100.6334 | 1 | 100.6334 | 1 | 100.6334 | 1 | 100.6334 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| h) | Cable ducts | Lump Sum | 90.5701 | 0.9 | 81.5131 | 1.05 | 95.0986 | 1 | 90.5701 | 1 | 90.5701 | 0.85 | 76.9846 | 0.85 | 76.9846 | 1.2 | 108.6841 | 1.25 | 113.2126 | 1.5 | 135.8551 | 1.2 | 108.6841 | 0.78 | 70.6447 | 0.78 | 70.6447 | 0.85 | 76.9846 | 1.3 | 117.7411 | 1.23 | 111.4012 | 0.85 | 76.9846 | 0.85 | 76.9846 | 1.5 | 135.8551 | 0.6 | 54.342 | 0.5 | 45.285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| i) | Providing water supply including drinking water & water for fire fighting system and sewage system | Lump Sum | 5.5711 | 1 | 5.5711 | 1 | 5.5711 | 1 | 5.5711 | 1 | 5.5711 | 1 | 5.5711 | 1 | 5.5711 | 1 | 5.5711 | 1 | 5.5711 | 1 | 5.5711 | 1 | 5.5711 | 1 | 5.5711 | 1 | 5.5711 | 1 | 5.5711 | 1 | 5.5711 | 1 | 5.5711 | 1 | 5.5711 | 1 | 5.5711 | 1 | 5.5711 | 1 | 5.5711 | 1 | 5.5711 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| j) | Parking sheds,Rain water Harvesting systems & land scaping etc., | Lump Sum | 30.19 | 1 | 30.19 | 1 | 30.19 | 1 | 30.19 | 1 | 30.19 | 1 | 30.19 | 1 | 30.19 | 1.1 | 33.209 | 1.1 | 33.209 | 1.1 | 33.209 | 1.1 | 33.209 | 1 | 30.19 | 1 | 30.19 | 1 | 30.19 | 1.1 | 33.209 | 1 | 30.19 | 1 | 30.19 | 1 | 30.19 | 1 | 30.19 | 1 | 30.19 | 1 | 30.19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Sub-Total -1-A | INR Lakhs |  |  | 483.5546 |  | 497.1401 |  | 480.5327 |  | 489.5052 |  | 437.5178 |  | 437.5178 |  | 538.956 |  | 562.9262 |  | 653.5322 |  | 550.671 |  | 443.3435 |  | 437.2607 |  | 443.6006 |  | 559.728 |  | 513.4427 |  | 437.5178 |  | 443.4888 |  | 738.2756 |  | 448.4901 |  | 421.6549 |  | 1.0798 |  | 1.0798 |  | 0.71983 |  | 3.2393 |  | 0 |  | 1.0798
| 1-B | Electrical works
| a) | A.C.Supply
| i | LT Switch Gear consisting of 415 V main switch board, ACDB, MLDB, Emergency LDB, A/C DB, 220 V DCDB, 50V DCDB, 1 trasformer each of rating 630KVA, 11kV/440V and 800KVA, 33KV/440V,72.5KV Isolator, CT, PT, CB/Fuse 33KV and 11KV Isolator, fuse, SA | Set | 69.3932 | 1 | 69.3932 | 1 | 69.3932 | 1 | 69.3932 | 1 | 69.3932 | 1 | 69.3932 | 1 | 69.3932 | 1 | 69.3932 | 1 | 69.3932 | 1 | 69.3932 | 1 | 69.3932 | 1 | 69.3932 | 1 | 69.3932 | 1 | 69.3932 | 1 | 69.3932 | 1 | 69.3932 | 1 | 69.3932 | 1 | 69.3932 | 1 | 69.3932 | 1 | 69.3932 | 1 | 69.3932 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ii | Foundations for 1of 630KVA 33/0.415 kV and one of 800kVA 33/0.415kv LT transformer, BM Kiosk etc. | LumpSum | 0.20127 | 1 | 0.20127 | 1 | 0.20127 | 1 | 0.20127 | 1 | 0.20127 | 1 | 0.20127 | 1 | 0.20127 | 1 | 0.20127 | 1 | 0.20127 | 1 | 0.20127 | 1 | 0.20127 | 1 | 0.20127 | 1 | 0.20127 | 1 | 0.20127 | 1 | 0.20127 | 1 | 0.20127 | 1 | 0.20127 | 1 | 0.20127 | 1 | 0.20127 | 1 | 0.20127 | 1 | 0.20127 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) | Station D.C Batteries 220 V, 500 AH | Set | 6.4504 | 2 | 12.9009 | 2 | 12.9009 | 2 | 12.9009 | 2 | 12.9009 | 2 | 12.9009 | 2 | 12.9009 | 2 | 12.9009 | 2 | 12.9009 | 2 | 12.9009 | 2 | 12.9009 | 2 | 12.9009 | 2 | 12.9009 | 2 | 12.9009 | 2 | 12.9009 | 2 | 12.9009 | 2 | 12.9009 | 2 | 12.9009 | 2 | 12.9009 | 1 | 6.4504 | 1 | 6.4504 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| c) | Station D.C Batteries 50 V, 500 AH | Set | 2.4136 | 2 | 4.8272 | 2 | 4.8272 | 2 | 4.8272 | 2 | 4.8272 | 2 | 4.8272 | 2 | 4.8272 | 2 | 4.8272 | 2 | 4.8272 | 2 | 4.8272 | 2 | 4.8272 | 2 | 4.8272 | 2 | 4.8272 | 2 | 4.8272 | 2 | 4.8272 | 2 | 4.8272 | 2 | 4.8272 | 2 | 4.8272 | 2 | 4.8272 | 1 | 2.4136 | 1 | 2.4136 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| d) | Battery Charger System 220 V, 70A / 50 A Float cum Boost | Set | 2.6198 | 2 | 5.2396 | 2 | 5.2396 | 2 | 5.2396 | 2 | 5.2396 | 2 | 5.2396 | 2 | 5.2396 | 2 | 5.2396 | 2 | 5.2396 | 2 | 5.2396 | 2 | 5.2396 | 2 | 5.2396 | 2 | 5.2396 | 2 | 5.2396 | 2 | 5.2396 | 2 | 5.2396 | 2 | 5.2396 | 2 | 5.2396 | 2 | 5.2396 | 1 | 2.6198 | 1 | 2.6198 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| e) | Battery Charger System 50 V, 70 A / 50 A Float cum Boost | Set | 1.7573 | 2 | 3.5146 | 2 | 3.5146 | 2 | 3.5146 | 2 | 3.5146 | 2 | 3.5146 | 2 | 3.5146 | 2 | 3.5146 | 2 | 3.5146 | 2 | 3.5146 | 2 | 3.5146 | 2 | 3.5146 | 2 | 3.5146 | 2 | 3.5146 | 2 | 3.5146 | 2 | 3.5146 | 2 | 3.5146 | 2 | 3.5146 | 2 | 3.5146 | 1 | 1.7573 | 1 | 1.7573 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| f) | Sub-Station Automation including Hardware, software, Remote Control Station, DMT scheme along with associated equipment and kiosks | Set | 250 | 1.38 | 345 | 1.532 | 383 | 1.684 | 421 | 1.38 | 345 | 1.152 | 288 | 1.076 | 269 | 1.76 | 440 | 1.532 | 383 | 2.824 | 706 | 1.968 | 492 | 1.076 | 269 | 1.152 | 288 | 1 | 250 | 1.988 | 497 | 1.836 | 459 | 1 | 250 | 1.152 | 288 | 2.824 | 706 | 1 | 250 | 1 | 250 | 0.152 | 38 | 0.152 | 38 | 0.076 | 19 | 0.228 | 57 | 0.076 | 19 | 0.152 | 38
| g) | Power Cables | Km | 1.223 | 44.5 | 54.4231 | 44.5 | 54.4231 | 48.6 | 59.4373 | 40.1 | 49.0419 | 34 | 41.5817 | 30.6 | 37.4235 | 51.18 | 62.5927 | 72 | 88.0553 | 121.5 | 148.5934 | 61.4 | 75.0916 | 30.6 | 37.4235 | 30.6 | 37.4235 | 30.6 | 37.4235 | 86 | 105.1772 | 56.14 | 68.6587 | 34 | 41.5817 | 34 | 41.5817 | 121.5 | 148.5934 | 25.59 | 31.2963 | 19.1925 | 23.4722 | 4 | 4.892 | 2.5 | 3.0575 | 2 | 2.446 | 4.5 | 5.5035 | 2.5 | 3.0575 | 4 | 4.892
| h) | Control Cables | Km | 1.0192 | 90 | 91.7243 | 90 | 91.7243 | 106 | 108.0308 | 76.5 | 77.9657 | 61 | 62.1687 | 51.85 | 52.8434 | 108 | 110.0692 | 143 | 145.7397 | 238.5 | 243.0694 | 140.4 | 143.0899 | 55 | 56.0537 | 55 | 56.0537 | 51.85 | 52.8434 | 200 | 203.8318 | 115 | 117.2033 | 61 | 62.1687 | 61 | 62.1687 | 238.5 | 243.0694 | 54 | 55.0346 | 40.5 | 41.2759 | 8 | 8.1533 | 5 | 5.0958 | 4 | 4.0766 | 9 | 9.1724 | 8 | 8.1533 | 8 | 8.1533
| J | Earth mat - 40mm dia MS rods | Km | 5.8481 | 27.7 | 161.9921 | 27.7 | 161.9921 | 27.7 | 161.9921 | 26.59 | 155.5007 | 22 | 128.658 | 22 | 128.658 | 32.5 | 190.0629 | 37.5 | 219.3034 | 60.7 | 354.9791 | 36.9 | 215.7945 | 26.59 | 155.5007 | 24.3 | 142.1086 | 24.29 | 142.0501 | 36.9 | 215.7945 | 27.7 | 161.9921 | 22 | 128.658 | 24.29 | 142.0501 | 50.8 | 297.083 | 21.4434 | 125.4029 | 16.0826 | 94.0522 | 1.5 | 8.7721 | 1.5 | 8.7721 | 0.4 | 2.3392 | 2.7 | 15.7898 | 1.7 | 9.9418 | 1.7 | 9.9418
| k) | Diesel Generator set along with AMF panel 250 kVA | Set | 20.2349 | 1 | 20.2349 | 1 | 20.2349 | 1 | 20.2349 | 1 | 20.2349 | 1 | 20.2349 | 1 | 20.2349 | 1 | 20.2349 | 1 | 20.2349 | 1 | 20.2349 | 1 | 20.2349 | 1 | 20.2349 | 1 | 20.2349 | 1 | 20.2349 | 1 | 20.2349 | 1 | 20.2349 | 1 | 20.2349 | 1 | 20.2349 | 1 | 20.2349 | 1 | 20.2349 | 1 | 20.2349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| l) | A/C and ventilation - High Valve Type split AC unit of 2TR capacity | No. | 0.36 | 12 | 4.32 | 12 | 4.32 | 12 | 4.32 | 12 | 4.32 | 12 | 4.32 | 12 | 4.32 | 12 | 4.32 | 12 | 4.32 | 12 | 4.32 | 12 | 4.32 | 12 | 4.32 | 12 | 4.32 | 12 | 4.32 | 12 | 4.32 | 12 | 4.32 | 12 | 4.32 | 12 | 4.32 | 12 | 4.32 | 1 | 0.36 | 1 | 0.36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| m) | Fire fighting system | 1 | 75 | 1 | 75 | 1.13 | 84.75 | 1.27 | 95.25 | 1.13 | 84.75 | 1.13 | 84.75 | 1 | 75 | 1.13 | 84.75 | 1.47 | 110.25 | 2 | 150 | 1.25 | 93.75 | 1.07 | 80.25 | 1.06 | 79.5 | 1 | 75 | 1.92 | 144 | 1.33 | 99.75 | 1 | 75 | 1.2 | 90 | 1.4 | 105 | 1 | 75 | 1 | 75 | 0.07 | 5.25 | 0 | 0 | 0 | 0 | 0.13 | 9.75 | 0.1 | 7.5 | 0.15 | 11.25
| o) | Illumination System - Indoor and Outdoor | Lump Sum | 55 | 1 | 55 | 1 | 55 | 1 | 55 | 1 | 55 | 1 | 55 | 1 | 55 | 1 | 55 | 1 | 55 | 1 | 55 | 1 | 55 | 1 | 55 | 1 | 55 | 1 | 55 | 1 | 55 | 1 | 55 | 1 | 55 | 1 | 55 | 1 | 55 | 0.66 | 36.3 | 0.66 | 36.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| p) | Mandatory spares | Lump Sum | 175 | 1 | 175 | 1.2 | 210 | 1.2 | 210 | 0.87 | 152.25 | 1.2 | 210 | 1.1 | 192.5 | 1.2 | 210 | 1.5 | 262.5 | 2 | 350 | 1.2 | 210 | 1.2 | 210 | 1.2 | 210 | 1.2 | 210 | 1.2 | 210 | 1.2 | 210 | 1 | 175 | 1.2 | 210 | 2 | 350 | 1 | 175 | 1 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Sub Total -1-B | INR Lakhs |  |  | 1078.771 |  | 1161.521 |  | 1231.3418 |  | 1040.1398 |  | 990.7899 |  | 931.0564 |  | 1273.1063 |  | 1384.48 |  | 2128.2734 |  | 1405.3576 |  | 983.8595 |  | 988.7174 |  | 942.9486 |  | 1551.4351 |  | 1292.2356 |  | 908.0399 |  | 1009.432 |  | 2025.3773 |  | 851.4643 |  | 798.5308 |  | 65.0674 |  | 54.9254 |  | 27.8619 |  | 97.2157 |  | 47.6525 |  | 72.237
| 1-C | Erection charges
| a) | Auxiliary Transformers,LT Switchgear, AC & DC Panels.72.5 kV ,33kV, & 11 kV equipments Etc | Set | 2.2285 | 1 | 2.2285 | 1 | 2.2285 | 1 | 2.2285 | 1 | 2.2285 | 1 | 2.2285 | 1 | 2.2285 | 1 | 2.2285 | 1 | 2.2285 | 1 | 2.2285 | 1 | 2.2285 | 1 | 2.2285 | 1 | 2.2285 | 1 | 2.2285 | 1 | 2.2285 | 1 | 2.2285 | 1 | 2.2285 | 1 | 2.2285 | 1 | 2.2285 | 1 | 2.2285 | 1 | 2.2285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) | Station D.C Batteries 220 V, 500 AH | Set | 0.27811 | 2 | 0.55622 | 2 | 0.55622 | 2 | 0.55622 | 2 | 0.55622 | 2 | 0.55622 | 2 | 0.55622 | 2 | 0.55622 | 2 | 0.55622 | 2 | 0.55622 | 2 | 0.55622 | 2 | 0.55622 | 2 | 0.55622 | 2 | 0.55622 | 2 | 0.55622 | 2 | 0.55622 | 2 | 0.55622 | 2 | 0.55622 | 2 | 0.55622 | 2 | 0.55622 | 2 | 0.55622 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| c) | Station D.C Batteries 50 V, 500 AH | Set | 0.11588 | 2 | 0.23176 | 2 | 0.23176 | 2 | 0.23176 | 2 | 0.23176 | 2 | 0.23176 | 2 | 0.23176 | 2 | 0.23176 | 2 | 0.23176 | 2 | 0.23176 | 2 | 0.23176 | 2 | 0.23176 | 2 | 0.23176 | 2 | 0.23176 | 2 | 0.23176 | 2 | 0.23176 | 2 | 0.23176 | 2 | 0.23176 | 2 | 0.23176 | 2 | 0.23176 | 2 | 0.23176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| d) | Battery Charger System 220 V, 70A / 50 A Float cum Boost | Set | 0.22285 | 2 | 0.44569 | 2 | 0.44569 | 2 | 0.44569 | 2 | 0.44569 | 2 | 0.44569 | 2 | 0.44569 | 2 | 0.44569 | 2 | 0.44569 | 2 | 0.44569 | 2 | 0.44569 | 2 | 0.44569 | 2 | 0.44569 | 2 | 0.44569 | 2 | 0.44569 | 2 | 0.44569 | 2 | 0.44569 | 2 | 0.44569 | 2 | 0.44569 | 2 | 0.44569 | 2 | 0.44569 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| e) | Battery Charger System 50 V, 70 A / 50 A Float cum Boost | Set | 0.16713 | 2 | 0.33427 | 2 | 0.33427 | 2 | 0.33427 | 2 | 0.33427 | 2 | 0.33427 | 2 | 0.33427 | 2 | 0.33427 | 2 | 0.33427 | 2 | 0.33427 | 2 | 0.33427 | 2 | 0.33427 | 2 | 0.33427 | 2 | 0.33427 | 2 | 0.33427 | 2 | 0.33427 | 2 | 0.33427 | 2 | 0.33427 | 2 | 0.33427 | 2 | 0.33427 | 2 | 0.33427 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| f) | Sub-Station Automation including Hardware, software, Remote Control Station, DMT Scheme along with associated equipment and kiosks | Set | 7.7996 | 1 | 7.7996 | 1 | 7.7996 | 1 | 7.7996 | 1 | 7.7996 | 1 | 7.7996 | 1 | 7.7996 | 1 | 7.7996 | 1 | 7.7996 | 1 | 7.7996 | 1 | 7.7996 | 1 | 7.7996 | 1 | 7.7996 | 1 | 7.7996 | 1 | 7.7996 | 1 | 7.7996 | 1 | 7.7996 | 1 | 7.7996 | 1 | 7.7996 | 1 | 7.7996 | 1 | 7.7996 | 0.06 | 0.46798 | 0.06 | 0.46798 | 0.06 | 0.46798 | 0.1 | 0.77996 | 0.06 | 0.46798 | 0.06 | 0.46798
| g) | Power cables | Set | 4.4569 | 1 | 4.4569 | 1 | 4.4569 | 1.1 | 4.9026 | 0.9 | 4.0112 | 0.75 | 3.3427 | 0.69 | 3.0753 | 1.15 | 5.1254 | 1.62 | 7.2202 | 2.7 | 12.0337 | 1.38 | 6.1505 | 0.69 | 3.0753 | 0.69 | 3.0753 | 0.69 | 3.0753 | 1.93 | 8.6018 | 1.26 | 5.6157 | 0.75 | 3.3427 | 0.75 | 3.3427 | 2.7 | 12.0337 | 0.575 | 2.5627 | 0.43125 | 1.922 | 0.09 | 0.40112 | 0.056 | 0.24959 | 0.045 | 0.20056 | 0.1 | 0.44569 | 0.09 | 0.40112 | 0.09 | 0.40112
| h) | Control cables | Set | 6.6854 | 1 | 6.6854 | 1 | 6.6854 | 1.18 | 7.8887 | 0.77 | 5.1477 | 0.68 | 4.5461 | 0.58 | 3.8775 | 1.2 | 8.0224 | 1.59 | 10.6297 | 2.65 | 17.7162 | 1.56 | 10.4292 | 0.61 | 4.0781 | 0.61 | 4.0781 | 0.58 | 3.8775 | 2.22 | 14.8415 | 1.28 | 8.5573 | 0.68 | 4.5461 | 0.68 | 4.5461 | 2.65 | 17.7162 | 0.6 | 4.0112 | 0.45 | 3.0084 | 0.09 | 0.60168 | 0.056 | 0.37438 | 0.045 | 0.30084 | 0.1 | 0.66854 | 0.09 | 0.60168 | 0.09 | 0.60168
| i) | Earth mat formation | Set | 16.7134 | 1 | 16.7134 | 1 | 16.7134 | 1 | 16.7134 | 1 | 16.7134 | 1 | 16.7134 | 1 | 16.7134 | 1.2 | 20.0561 | 1.5 | 25.0701 | 2.5 | 41.7836 | 1.2 | 20.0561 | 1 | 16.7134 | 1 | 16.7134 | 1 | 16.7134 | 1.2 | 20.0561 | 1 | 16.7134 | 1 | 16.7134 | 1.1 | 18.3848 | 2.5 | 41.7836 | 0.792 | 13.237 | 0.594 | 9.9278 | 0.16 | 2.6741 | 0.0162 | 0.27076 | 0.045 | 0.7521 | 0.22 | 3.677 | 0.16 | 2.6741 | 0.16 | 2.6741
| j) | Diesel Generator set with AMF panel 250 kVA | Set | 0.66854 | 1 | 0.66854 | 1 | 0.66854 | 1 | 0.66854 | 1 | 0.66854 | 1 | 0.66854 | 1 | 0.66854 | 1 | 0.66854 | 1 | 0.66854 | 1 | 0.66854 | 1 | 0.66854 | 1 | 0.66854 | 1 | 0.66854 | 1 | 0.66854 | 1 | 0.66854 | 1 | 0.66854 | 1 | 0.66854 | 1 | 0.66854 | 1 | 0.66854 | 1 | 0.66854 | 1 | 0.66854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| k) | Air Conditioning and Ventilation | Set | 1.0028 | 1 | 1.0028 | 1 | 1.0028 | 1 | 1.0028 | 1 | 1.0028 | 1 | 1.0028 | 1 | 1.0028 | 1 | 1.0028 | 1 | 1.0028 | 1 | 1.0028 | 1 | 1.0028 | 1 | 1.0028 | 1 | 1.0028 | 1 | 1.0028 | 1 | 1.0028 | 1 | 1.0028 | 1 | 1.0028 | 1 | 1.0028 | 1 | 1.0028 | 1 | 1.0028 | 1 | 1.0028 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| l) | Fire Fighting System | Set | 8.9138 | 1 | 8.9138 | 1.35 | 12.0337 | 1.75 | 15.5992 | 1.35 | 12.0337 | 1.35 | 12.0337 | 1 | 8.9138 | 1.35 | 12.0337 | 1.75 | 15.5992 | 2.5 | 22.2846 | 1.35 | 12.0337 | 1 | 8.9138 | 1 | 8.9138 | 1 | 8.9138 | 1 | 8.9138 | 1 | 8.9138 | 1 | 8.9138 | 1.35 | 12.0337 | 2.5 | 22.2846 | 1 | 8.9138 | 1 | 8.9138 | 0.5 | 4.4569 | 0 | 0 | 0 | 0 | 0.5 | 4.4569 | 0.5 | 4.4569 | 0.5 | 4.4569
| n) | Illumination System - Indoor & outdoor | Set | 11.1423 | 1 | 11.1423 | 1 | 11.1423 | 1 | 11.1423 | 1 | 11.1423 | 1 | 11.1423 | 1 | 11.1423 | 1 | 11.1423 | 1 | 11.1423 | 1 | 11.1423 | 1 | 11.1423 | 1 | 11.1423 | 1 | 11.1423 | 1 | 11.1423 | 1 | 11.1423 | 1 | 11.1423 | 1 | 11.1423 | 1 | 11.1423 | 1 | 11.1423 | 0.66 | 7.3539 | 0.66 | 7.3539 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Sub Total -1-C | INR Lakhs |  |  | 61.1791 |  | 64.299 |  | 69.5136 |  | 62.3157 |  | 61.0454 |  | 56.9896 |  | 69.6473 |  | 82.9289 |  | 118.2276 |  | 73.0791 |  | 57.1902 |  | 57.1902 |  | 56.9896 |  | 76.8229 |  | 64.2098 |  | 57.9256 |  | 62.7168 |  | 118.2276 |  | 49.346 |  | 44.3933 |  | 8.6018 |  | 1.3627 |  | 1.7215 |  | 10.0281 |  | 8.6018 |  | 8.6018
|  | Total -1 | INR Lakhs |  |  | 1623.5048 |  | 1722.9601 |  | 1781.3881 |  | 1591.9607 |  | 1489.3532 |  | 1425.5639 |  | 1881.7096 |  | 2030.335 |  | 2900.0333 |  | 2029.1077 |  | 1484.3932 |  | 1483.1683 | 1 | 1443.5388 | 1 | 2187.986 |  | 1869.8882 |  | 1403.4833 |  | 1515.6376 |  | 2881.8805 |  | 1349.3004 |  | 1264.579 |  | 74.749 |  | 57.3679 |  | 30.3032 |  | 110.483 |  | 56.2543 |  | 81.9186
| 2 | ICTs
| a) | I.C.T 315 MVA, 3Phase, 400/220/33 KV class | No. | 869.9688 | 2 | 1739.9375 | 2 | 1739.9375 | 2 | 1739.9375 | 2 | 1739.9375 | 2 | 1739.9375 | 1 | 869.9688 | 2 | 1739.9375 | 0 | 0 | 0 | 0 | 2 | 1739.9375 | 2 | 1739.9375 | 2 | 1739.9375 | 1 | 869.9688 | 0 | 0 | 3 | 2609.9063 | 2 | 1739.9375 | 2 | 1739.9375 | 2 | 1739.9375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 869.9688 | 0 | 0 | 0 | 0
| b) | I.C.T 167 MVA, S-Phase, 400/220/33 kV (Single Phase 167 MVA Units) | No. | 488.9265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 1955.706 | 7 | 3422.4855 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 3422.4855 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| d) | Erection Charges | Nos | 6.6854 | 2 | 13.3707 | 2 | 13.3707 | 2 | 13.3707 | 2 | 13.3707 | 2 | 13.3707 | 1 | 6.6854 | 2 | 13.3707 | 4 | 26.7415 | 7 | 46.7976 | 2 | 13.3707 | 2 | 13.3707 | 2 | 13.3707 | 1 | 6.6854 | 7 | 46.7976 | 3 | 20.0561 | 2 | 13.3707 | 2 | 13.3707 | 2 | 13.3707 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 6.6854 | 0 | 0 | 0 | 0
| e) | Foundations | Nos | 15.095 | 2 | 30.19 | 2 | 30.19 | 2 | 30.19 | 2 | 30.19 | 2 | 30.19 | 1 | 15.095 | 2 | 30.19 | 4 | 60.3801 | 7 | 105.6651 | 2 | 30.19 | 2 | 30.19 | 2 | 30.19 | 1 | 15.095 | 7 | 105.6651 | 3 | 45.285 | 2 | 30.19 | 2 | 30.19 | 2 | 30.19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 15.095 | 0 | 0 | 0 | 0
| f) | Fire wall between the Transformers | Nos | 1.0063 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 3.019 | 4 | 4.0253 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 4.0253 | 1 | 1.0063 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Total -2 | INR Lakhs |  |  | 1783.4983 |  | 1783.4983 |  | 1783.4983 |  | 1783.4983 |  | 1783.4983 |  | 891.7492 |  | 1783.4983 |  | 2045.8465 |  | 3578.9735 |  | 1783.4983 |  | 1783.4983 |  | 1783.4983 |  | 891.7492 |  | 3578.9735 |  | 2676.2538 |  | 1783.4983 |  | 1783.4983 |  | 1783.4983 | 0 | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 891.7492 |  | 0 |  | 0
| 3 | Shunt & Bus Reactors Reactors
| 3-A | Shunt Reactors
| a) | Shunt Reactor 420 kV 63/50 MVAR | No. | 340.5353 | 0 | 0 | 2 | 681.0706 | 4 | 1362.1413 | 2 | 681.0706 | 2 | 681.0706 | 2 | 681.0706 | 2 | 681.0706 | 3 | 1021.6059 | 5 | 1702.6766 | 2 | 681.0706 | 1 | 340.5353 | 0 | 0 | 1 | 340.5353 | 2 | 681.0706 | 2 | 681.0706 | 0 | 0 | 2 | 681.0706 | 4 | 1362.1413 | 2 | 681.0706 | 2 | 681.0706 | 1 | 340.5353 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 340.5353 | 0 | 0
| b) | Shunt Reactor 420 kV 80 MVAR | No. | 378.1723 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| c) | Shunt Reactor 420 kV 125 MVAR | No. | 396.3704 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| d) | NGR,145KV | No. | 24.3159 | 0 | 0 | 2 | 48.6319 | 4 | 97.2637 | 2 | 48.6319 | 2 | 48.6319 | 2 | 48.6319 | 2 | 48.6319 | 3 | 72.9478 | 5 | 121.5797 | 2 | 48.6319 | 1 | 24.3159 | 0 | 0 | 1 | 24.3159 | 2 | 48.6319 | 2 | 48.6319 | 0 | 0 | 2 | 48.6319 | 4 | 97.2637 | 2 | 48.6319 | 2 | 48.6319 | 1 | 24.3159 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 24.3159 | 0 | 0
| e) | Surge Arrestors 120 kV for NGR | No. | 1.5995 | 0 | 0 | 2 | 3.1989 | 4 | 6.3979 | 2 | 3.1989 | 2 | 3.1989 | 2 | 3.1989 | 2 | 3.1989 | 3 | 4.7984 | 5 | 7.9974 | 2 | 3.1989 | 1 | 1.5995 | 0 | 0 | 1 | 1.5995 | 2 | 3.1989 | 2 | 3.1989 | 0 | 0 | 2 | 3.1989 | 4 | 6.3979 | 2 | 3.1989 | 2 | 3.1989 | 1 | 1.5995 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1.5995 | 0 | 0
| f) | Errection Charges | Set | 4.4569 | 0 | 0 | 2 | 8.9138 | 4 | 17.8277 | 2 | 8.9138 | 2 | 8.9138 | 2 | 8.9138 | 2 | 8.9138 | 3 | 13.3707 | 5 | 22.2846 | 2 | 8.9138 | 1 | 4.4569 | 0 | 0 | 1 | 4.4569 | 2 | 8.9138 | 2 | 8.9138 | 0 | 0 | 2 | 8.9138 | 4 | 17.8277 | 2 | 8.9138 | 2 | 8.9138 | 1 | 4.4569 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 4.4569 | 0 | 0
| g) | Foundation for 400 kV Shunt Reactors with NGR | No. | 10.0633 | 0 | 0 | 2 | 20.1267 | 4 | 40.2534 | 2 | 20.1267 | 2 | 20.1267 | 2 | 20.1267 | 2 | 20.1267 | 3 | 30.19 | 5 | 50.3167 | 2 | 20.1267 | 1 | 10.0633 | 0 | 0 | 1 | 10.0633 | 2 | 20.1267 | 2 | 20.1267 | 0 | 0 | 2 | 20.1267 | 4 | 40.2534 | 2 | 20.1267 | 2 | 20.1267 | 1 | 10.0633 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 10.0633 | 0 | 0
|  | Sub-Total -3-A | INR Lakhs |  |  | 0 |  | 761.942 |  | 1523.8839 |  | 761.942 |  | 761.942 |  | 761.942 |  | 761.942 |  | 1142.9129 |  | 1904.8549 |  | 761.942 |  | 380.971 |  | 0 |  | 380.971 |  | 761.942 |  | 761.942 |  | 0 |  | 761.942 |  | 1523.8839 |  | 761.942 |  | 761.942 |  | 380.971 |  | 0 |  | 0 |  | 0 |  | 380.971 |  | 0
| 3-B | Bus Reactors
| a) | Bus Reactor, 420KV, 63 / 50 MVAR | No. | 340.5353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 681.0706 | 0 | 0 |  | 0 | 1 | 340.5353 | 2 | 681.0706 | 1 | 340.5353 | 0 | 0 | 1 | 340.5353 | 2 | 681.0706 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 340.5353
| b) | Bus Reactor, 420KV, 80 MVAR | No. | 378.1723 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 1 | 378.1723 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 1 | 378.1723 | 1 | 378.1723 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
| c) | Bus Reactor, 420KV, 125 MVAR | No. | 396.3704 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
| d) | Errection Charges | No. | 4.4569 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 8.9138 | 0 | 0 | 1 | 4.4569 | 1 | 4.4569 | 2 | 8.9138 | 1 | 4.4569 | 0 | 0 | 1 | 4.4569 | 2 | 8.9138 | 1 | 4.4569 | 1 | 4.4569 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 4.4569
| e) | Foundation for 400 kV Bus Reactors | No. | 10.0633 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 20.1267 | 0 | 0 | 1 | 10.0633 | 1 | 10.0633 | 2 | 20.1267 | 1 | 10.0633 | 0 | 0 | 1 | 10.0633 | 2 | 20.1267 | 1 | 10.0633 | 1 | 10.0633 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 10.0633
|  | Sub-Total -3-B | INR Lakhs |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 710.1111 |  | 0 |  | 392.6926 |  | 355.0556 |  | 710.1111 |  | 355.0556 |  | 0 |  | 355.0556 |  | 710.1111 |  | 392.6926 |  | 392.6926 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 355.0556
|  | Total -3 | INR Lakhs |  |  | 0 |  | 761.942 |  | 1523.8839 |  | 761.942 |  | 761.942 |  | 761.942 |  | 761.942 |  | 1142.9129 |  | 1904.8549 |  | 1472.0531 |  | 380.971 |  | 392.6926 |  | 736.0265 |  | 1472.0531 |  | 1116.9975 |  | 0 |  | 1116.9975 |  | 2233.9951 |  | 1154.6345 |  | 1154.6345 |  | 380.971 |  | 0 |  | 0 |  | 0 |  | 380.971 |  | 355.0556
| 4 | 400 kV Bays & Equipments
| 4-A | 400 KV Equipments
| a) | 420 KV,2000A, 40KA CB without CR & with support structure | No. | 46.2398 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 323.6788 | 9 | 416.1585 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 924.7966 | 11 | 508.6382 | 6 | 277.439 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) | 420 KV,2000A, 40KA CB without CR & with support structure | No. | 42.403 | 9 | 381.6272 | 11 | 466.4333 | 13 | 551.2393 | 11 | 466.4333 | 8 | 339.2242 | 7 | 296.8212 | 14 | 593.6423 | 4 | 169.6121 | 13 | 551.2393 | 17 | 720.8514 | 7 | 296.8212 | 8 | 339.2242 | 7 | 296.8212 | 17 | 720.8514 | 14 | 593.6423 | 6 | 254.4181 | 8 | 339.2242 | 9 | 381.6272 | 1 | 42.403 | 2 | 84.806 | 1.5 | 63.6045 | 1.5 | 63.6045 | 0 | 0 | 1.5 | 63.6045 | 1 | 42.403 | 1.5 | 63.6045
| c) | 420 kV CT 2000A, 40KA, 5-Core with 120% extended current | No. | 7.5111 | 30 | 225.3341 | 30 | 225.3341 | 30 | 225.3341 | 30 | 225.3341 | 18 | 135.2004 | 15 | 112.667 | 42 | 315.4677 | 27 | 202.8007 | 60 | 450.6681 | 51 | 383.0679 | 18 | 135.2004 | 24 | 180.2673 | 12 | 90.1336 | 48 | 360.5345 | 39 | 292.9343 | 18 | 135.2004 | 24 | 180.2673 | 87 | 653.4688 | 45 | 338.0011 | 30 | 225.3341 | 4.5 | 33.8001 | 4.5 | 33.8001 | 0 | 0 | 4.5 | 33.8001 | 0 | 0 | 6 | 45.0668
| d) | CVT | [38 empty] | 0 |  | 0
| i | 420 kV CVT 4400 PF | No. | 5.4346 | 12 | 65.2155 | 12 | 65.2155 | 12 | 65.2155 | 12 | 65.2155 | 6 | 32.6077 | 6 | 32.6077 | 18 | 97.8232 | 12 | 65.2155 | 27 | 146.7348 | 18 | 97.8232 | 6 | 32.6077 | 6 | 32.6077 | 6 | 32.6077 | 18 | 97.8232 | 12 | 65.2155 | 6 | 32.6077 | 6 | 32.6077 | 6 | 32.6077 | 6 | 32.6077 | 6 | 32.6077 | 3 | 16.3039 | 3 | 16.3039 | 0 | 0 | 0 | 0 | 3 | 16.3039 | 0 | 0
| ii | 420 kV CVT 8800 PF | No. | 6.8105 | 6 | 40.8629 | 6 | 40.8629 | 6 | 40.8629 | 6 | 40.8629 | 6 | 40.8629 | 6 | 40.8629 | 6 | 40.8629 | 6 | 40.8629 | 6 | 40.8629 | 6 | 40.8629 | 6 | 40.8629 | 6 | 40.8629 | 6 | 40.8629 | 6 | 40.8629 | 6 | 40.8629 | 6 | 40.8629 | 6 | 40.8629 | 36 | 245.1771 | 21 | 143.02 | 12 | 81.7257 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| e) | Isolators | No. | [37 empty] | 0 |  | 0
| i | 420 KV,2000 A,40 kA Isolator, DB Type with one E/S (3phase) | No. | 9.4556 | 22 | 208.023 | 24 | 226.9341 | 26 | 245.8453 | 24 | 226.9341 | 16 | 151.2894 | 13 | 122.9227 | 32 | 302.5789 | 23 | 217.4785 | 47 | 444.4127 | 40 | 378.2236 | 15 | 141.8338 | 19 | 179.6562 | 15 | 141.8338 | 40 | 378.2236 | 32 | 302.5789 | 14 | 132.3782 | 19 | 179.6562 | 70 | 661.8912 | 32 | 302.5789 | 21 | 198.5674 | 5 | 47.2779 | 4 | 37.8224 | 0 | 0 | 4 | 37.8224 | 1 | 9.4556 | 5 | 47.2779
| ii | 420 KV,2000A,40 kA Isolator one Phase with one E/S | No. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| iii | 420 KV,2000 A,40 kA Isolator, DB Type with two E/S (3phase) | No. | 10.8353 | 2 | 21.6707 | 2 | 21.6707 | 2 | 21.6707 | 2 | 21.6707 | 2 | 21.6707 | 2 | 21.6707 | 2 | 21.6707 | 2 | 21.6707 | 2 | 21.6707 | 2 | 21.6707 | 2 | 21.6707 | 2 | 21.6707 | 2 | 21.6707 | 2 | 21.6707 | 2 | 21.6707 | 2 | 21.6707 | 2 | 21.6707 | 2 | 21.6707 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| f) | Surge Arrestor 390 kV | No. | 1.8754 | 18 | 33.7563 | 24 | 45.0084 | 30 | 56.2606 | 24 | 45.0084 | 18 | 33.7563 | 18 | 33.7563 | 30 | 56.2606 | 24 | 45.0084 | 48 | 90.0169 | 36 | 67.5127 | 15 | 28.1303 | 15 | 28.1303 | 15 | 28.1303 | 36 | 67.5127 | 30 | 56.2606 | 12 | 22.5042 | 21 | 39.3824 | 60 | 112.5211 | 30 | 56.2606 | 21 | 39.3824 | 6 | 11.2521 | 3 | 5.6261 | 0 | 0 | 3 | 5.6261 | 3 | 5.6261 | 3 | 5.6261
| g) | PLCC equipments on 400 kV side (Both for 400 & 220 kV) | 1 | 76 | 1.71 | 129.96 | 1.71 | 129.96 | 1.71 | 129.96 | 1.42 | 107.92 | 1 | 76 | 1 | 76 | 2.13 | 161.88 | 2.45 | 186.2 | 5.96 | 452.96 | 2.13 | 161.88 | 1.42 | 107.92 | 1 | 76 | 1 | 76 | 2.13 | 161.88 | 1.71 | 129.96 | 1 | 76 | 1 | 76 | 3.25 | 247 | 1.4058 | 106.8408 | 1.14 | 86.64 | 0.25 | 19 | 0.25 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Sub Total - 4-A | INR Lakhs |  |  | 1106.4496 |  | 1221.4189 |  | 1336.3882 |  | 1199.3789 |  | 830.6116 |  | 737.3084 |  | 1590.1862 |  | 1272.5276 |  | 2614.7238 |  | 1871.8923 |  | 805.047 |  | 898.4192 |  | 728.0602 |  | 1849.3589 |  | 1503.125 |  | 715.6423 |  | 909.6713 |  | 3280.7605 |  | 1530.3502 |  | 1026.5023 |  | 191.2386 |  | 176.1569 |  | 0 |  | 140.8531 |  | 73.7885 |  | 161.5754
| 4-B | 400 kV Simplex type Panels
| a) | Circuit breaker relay panel With Auto reclosure | No. | 8.3151 | 7 | 58.206 | 7 | 58.206 | 7 | 58.206 | 7 | 58.206 | 4 | 33.2606 | 4 | 33.2606 | 10 | 83.1514 | 7 | 58.206 | 16 | 133.0422 | 10 | 83.1514 | 4 | 33.2606 | 4 | 33.2606 | 4 | 33.2606 | 11 | 91.4665 | 7 | 58.206 | 4 | 33.2606 | 4 | 33.2606 | 20 | 166.3028 | 11 | 91.4665 | 6 | 49.8908 | 1.5 | 12.4727 | 1.5 | 12.4727 | 0 | 0 | 0.5 | 4.1576 | 0 | 0 | 0 | 0
| b) | Circuit breaker relay panel Without Auto reclosure | No. | 6.607 | 2 | 13.2139 | 4 | 26.4278 | 4 | 26.4278 | 4 | 26.4278 | 4 | 26.4278 | 3 | 19.8209 | 4 | 26.4278 | 4 | 26.4278 | 7 | 46.2487 | 4 | 26.4278 | 3 | 19.8209 | 4 | 26.4278 | 3 | 19.8209 | 7 | 46.2487 | 7 | 46.2487 | 2 | 13.2139 | 4 | 26.4278 | 9 | 59.4626 | 1 | 6.607 | 2 | 13.2139 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 6.607 | 1 | 6.607 | 1.5 | 9.9104
| c) | Line protection panel | No's | 19.6415 | 4 | 78.566 | 4 | 78.566 | 4 | 78.566 | 4 | 78.566 | 2 | 39.283 | 2 | 39.283 | 6 | 117.849 | 4 | 78.566 | 9 | 176.7735 | 6 | 117.849 | 2 | 39.283 | 2 | 39.283 | 2 | 39.283 | 6 | 117.849 | 4 | 78.566 | 2 | 39.283 | 2 | 39.283 | 12 | 235.698 | 7 | 137.4905 | 4 | 78.566 | 1 | 19.6415 | 1 | 19.6415 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| d) | Reactor protection panel | Nos | 12.2936 | 0 | 0 | 2 | 24.5872 | 4 | 49.1744 | 2 | 24.5872 | 2 | 24.5872 | 2 | 24.5872 | 2 | 24.5872 | 3 | 36.8808 | 5 | 61.468 | 4 | 49.1744 | 1 | 12.2936 | 1 | 12.2936 | 2 | 24.5872 | 4 | 49.1744 | 3 | 36.8808 | 0 | 0 | 3 | 36.8808 | 6 | 73.7616 | 3 | 36.8808 | 3 | 36.8808 | 1 | 12.2936 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 12.2936 | 1 | 12.2936
| e) | Transformer Protection panel for both HV and MV sides | No. | 16.1881 | 2 | 32.3762 | 2 | 32.3762 | 2 | 32.3762 | 2 | 32.3762 | 2 | 32.3762 | 2 | 32.3762 | 2 | 32.3762 | 1 | 16.1881 | 2 | 32.3762 | 2 | 32.3762 | 2 | 32.3762 | 2 | 32.3762 | 2 | 32.3762 | 2 | 32.3762 | 3 | 48.5642 | 2 | 32.3762 | 2 | 32.3762 | 2 | 32.3762 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 16.1881 | 0 | 0 | 0 | 0
| f) | Double Bus Bar protection panel | No. | 107.1515 | 1 | 107.1515 | 1 | 107.1515 | 1 | 107.1515 | 1 | 107.1515 | 1 | 107.1515 | 1 | 107.1515 | 1 | 107.1515 | 1 | 107.1515 | 1 | 107.1515 | 1 | 107.1515 | 1 | 107.1515 | 1 | 107.1515 | 1 | 107.1515 | 1 | 107.1515 | 1 | 107.1515 | 1 | 107.1515 | 1 | 107.1515 | 1 | 107.1515 | 1 | 107.1515 | 1 | 107.1515 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Sub Total - 4-B | INR Lakhs |  |  | 289.5136 |  | 327.3147 |  | 351.9019 |  | 327.3147 |  | 263.0862 |  | 256.4793 |  | 391.5431 |  | 323.4202 |  | 557.0601 |  | 416.1303 |  | 244.1857 |  | 250.7926 |  | 256.4793 |  | 444.2663 |  | 375.6172 |  | 225.2851 |  | 275.3799 |  | 674.7527 |  | 379.5963 |  | 285.7031 |  | 44.4078 |  | 32.1142 |  | 0 |  | 26.9526 |  | 18.9006 |  | 22.204
| 4-C | 400 kV Towers, Beams & support structures - Lattice Type
| a) | Tower Type 4C1 - Number * Unit Weight | MT | 0.68144 | 25 | 17.0359 | 25 | 17.0359 | 25 | 17.0359 | 25 | 17.0359 | 15 | 10.2216 | 15 | 10.2216 | 35 | 23.8503 | 25 | 17.0359 | 65 | 44.2934 | 35 | 23.8503 | 15 | 10.2216 | 15 | 10.2216 | 15 | 10.2216 | 40 | 27.2575 | 25 | 17.0359 | 15 | 10.2216 | 15 | 10.2216 | 90 | 61.3293 | 45 | 30.6647 | 25 | 17.0359 | 7.5 | 5.1108 | 7.5 | 5.1108 | 0 | 0 | 10 | 6.8144 | 0 | 0 | 0 | 0
| b) | Tower Type 4C2 - Number * Unit Weight | MT | 0.68144 | 38 | 25.8946 | 38 | 25.8946 | 38 | 25.8946 | 38 | 25.8946 | 28.5 | 19.421 | 19 | 12.9473 | 38 | 25.8946 | 38 | 25.8946 | 36 | 24.5317 | 38 | 25.8946 | 28.5 | 19.421 | 28.5 | 19.421 | 19 | 12.9473 | 36 | 24.5317 | 45 | 30.6647 | 28.5 | 19.421 | 28.5 | 19.421 | 28.5 | 19.421 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 12.9473 | 0 | 0 | 0 | 0
| c) | Tower Type 4C3 - Number* Unit Weight | MT | 0.68144 | 72 | 49.0635 | 72 | 49.0635 | 72 | 49.0635 | 72 | 49.0635 | 38.25 | 26.065 | 45 | 30.6647 | 108 | 73.5952 | 72 | 49.0635 | 206.25 | 140.5464 | 108 | 73.5952 | 40.5 | 27.5982 | 58.5 | 39.8641 | 45 | 30.6647 | 136 | 92.6755 | 80.75 | 55.026 | 27 | 18.3988 | 40.5 | 27.5982 | 279 | 190.121 | 90 | 61.3293 | 76.5 | 52.1299 | 27 | 18.3988 | 27 | 18.3988 | 0 | 0 | 21 | 14.3102 | 0 | 0 | 36 | 24.5317
| d) | Beam Type 4B1 - Number * Unit Weight | MT | 0.68144 | 16 | 10.903 | 16 | 10.903 | 16 | 10.903 | 16 | 10.903 | 8 | 5.4515 | 8 | 5.4515 | 24 | 16.3545 | 16 | 10.903 | 25 | 17.0359 | 24 | 16.3545 | 8 | 5.4515 | 8 | 5.4515 | 8 | 5.4515 | 15 | 10.2216 | 10 | 6.8144 | 8 | 5.4515 | 8 | 5.4515 | 64 | 43.612 | 28 | 19.0802 | 16 | 10.903 | 4 | 2.7257 | 4 | 2.7257 | 0 | 0 | 4 | 2.7257 | 0 | 0 | 0 | 0
| e) | Beam Type 4B2 - Number * Unit Weight | MT | 0.68144 | 73.5 | 50.0856 | 73.5 | 50.0856 | 73.5 | 50.0856 | 73.5 | 50.0856 | 49 | 33.3904 | 38.5 | 26.2353 | 101.5 | 69.1659 | 70 | 47.7006 | 90 | 61.3293 | 101.5 | 69.1659 | 49 | 33.3904 | 63 | 42.9305 | 38.5 | 26.2353 | 85.25 | 58.0925 | 58.5 | 39.8641 | 42 | 28.6204 | 52.5 | 35.7755 | 203 | 138.3317 | 56 | 38.1605 | 45.5 | 31.0054 | 14 | 9.5401 | 14 | 9.5401 | 0 | 0 | 24.5 | 16.6952 | 0 | 0 | 14 | 9.5401
| f) | Lightning cum Lighting mast on both 400 & 220 kV switch Yard (6Nos *4.5 MT + 6Nos *3MT) | MT | 0.68144 | 45 | 30.6647 | 45 | 30.6647 | 45 | 30.6647 | 45 | 30.6647 | 45 | 30.6647 | 45 | 30.6647 | 45 | 30.6647 | 45 | 30.6647 | 45 | 30.6647 | 45 | 30.6647 | 45 | 30.6647 | 45 | 30.6647 | 45 | 30.6647 | 45 | 30.6647 | 45 | 30.6647 | 45 | 30.6647 | 45 | 30.6647 | 45 | 30.6647 | 27 | 18.3988 | 27 | 18.3988 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| g) | Equipment Support Structure - Number * Unit Weight | MT | 0.68144 | 28.2 | 19.2165 | 28.2 | 19.2165 | 30 | 20.4431 | 28.2 | 19.2165 | 16.8 | 11.4481 | 15 | 10.2216 | 43.2 | 29.4381 | 28.2 | 19.2165 | 63 | 42.9305 | 48.6 | 33.1178 | 16.8 | 11.4481 | 20.4 | 13.9013 | 13.2 | 8.995 | 48.6 | 33.1178 | 35.4 | 24.1229 | 16.8 | 11.4481 | 20.4 | 13.9013 | 88.2 | 60.1028 | 48 | 32.709 | 30 | 20.4431 | 6.6 | 4.4975 | 6.6 | 4.4975 | 0 | 0 | 1.5 | 1.0222 | 0 | 0 | 3.6 | 2.4532
|  | Sub Total - 4-C | INR Lakhs |  |  | 202.8638 |  | 202.8638 |  | 204.0904 |  | 202.8638 |  | 136.6622 |  | 126.4066 |  | 268.9632 |  | 200.4788 |  | 361.332 |  | 272.643 |  | 138.1955 |  | 162.4546 |  | 125.18 |  | 276.5613 |  | 204.1926 |  | 124.226 |  | 143.0337 |  | 543.5824 |  | 200.3425 |  | 149.9162 |  | 40.2729 |  | 40.2729 |  | 0 |  | 54.515 |  | 0 |  | 36.525
| 4-D | 400 KV Tubular type (Pipe) Equipment Support Structures
| a) | CVT - Number * Unit Weight | No/MT18*0.5MT | 0.90858 | 10.8 | 9.8127 | 10.8 | 9.8127 | 10.8 | 9.8127 | 10.8 | 9.8127 | 7.2 | 6.5418 | 7.2 | 6.5418 | 14.4 | 13.0836 | 10.8 | 9.8127 | 4.5 | 4.0886 | 14.4 | 13.0836 | 7.2 | 6.5418 | 7.2 | 6.5418 | 7.2 | 6.5418 | 12 | 10.903 | 9 | 8.1772 | 7.2 | 6.5418 | 7.2 | 6.5418 | 25.2 | 22.8963 | 16.2 | 14.719 | 10.8 | 9.8127 | 1.8 | 1.6354 | 1.8 | 1.6354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) | BPI - Number * Unit Weight | No/MT63*0.5MT | 0.90858 | 37.8 | 34.3444 | 37.8 | 34.3444 | 37.8 | 34.3444 | 37.8 | 34.3444 | 18 | 16.3545 | 16.8 | 15.2642 | 59.4 | 53.9698 | 59.4 | 53.9698 | 78 | 70.8695 | 59.4 | 53.9698 | 18 | 16.3545 | 21.6 | 19.6254 | 18 | 16.3545 | 49.5 | 44.9749 | 34.5 | 31.3461 | 18 | 16.3545 | 25.2 | 22.8963 | 64.8 | 58.8762 | 54 | 49.0635 | 27 | 24.5317 | 7.2 | 6.5418 | 7.2 | 6.5418 | 0 | 0 | 18 | 16.3545 | 3.6 | 3.2709 | 18 | 16.3545
| c) | Isolators - Number * Unit Weight | No/MT24*2.0MT | 0.90858 | 48 | 43.612 | 52 | 47.2463 | 48 | 43.612 | 52 | 47.2463 | 36 | 32.709 | 30 | 27.2575 | 68 | 61.7836 | 66 | 59.9665 | 112 | 101.7613 | 84 | 76.321 | 34 | 30.8918 | 42 | 38.1605 | 34 | 30.8918 | 84 | 76.321 | 68 | 61.7836 | 32 | 29.0747 | 42 | 38.1605 | 144 | 130.8359 | 51 | 46.3377 | 34.5 | 31.3461 | 10 | 9.0858 | 10 | 9.0858 | 0 | 0 | 10 | 9.0858 | 2 | 1.8172 | 10 | 9.0858
| d) | SA - Number * Unit Weight | No/MT18*0.5MT | 0.90858 | 10.8 | 9.8127 | 14.4 | 13.0836 | 18 | 16.3545 | 14.4 | 13.0836 | 10.8 | 9.8127 | 9 | 8.1772 | 18 | 16.3545 | 14.4 | 13.0836 | 24 | 21.806 | 21.6 | 19.6254 | 9 | 8.1772 | 9 | 8.1772 | 9 | 8.1772 | 18 | 16.3545 | 15 | 13.6287 | 7.2 | 6.5418 | 12.6 | 11.4481 | 36 | 32.709 | 18 | 16.3545 | 12.6 | 11.4481 | 3.6 | 3.2709 | 1.8 | 1.6354 | 0 | 0 | 1.8 | 1.6354 | 1.8 | 1.6354 | 1.8 | 1.6354
|  | Sub Total - 4-D | INR Lakhs |  |  | 97.5818 |  | 104.487 |  | 104.1236 |  | 104.487 |  | 65.418 |  | 57.2407 |  | 145.1915 |  | 136.8326 |  | 198.5254 |  | 162.9998 |  | 61.9654 |  | 72.5049 |  | 61.9654 |  | 148.5533 |  | 114.9357 |  | 58.5127 |  | 79.0467 |  | 245.3174 |  | 126.4747 |  | 77.1387 |  | 20.534 |  | 18.8985 |  | 0 |  | 27.0758 |  | 6.7235 |  | 27.0758
| 4-E | Bus Bar & Hard ware materials for 400 kV
| a) | 4" EH-IPS Alluminium Tube(OD- 114.2, ID-97.18) | L/S | 175.7157 | 1.8 | 316.2883 | 1.8 | 316.2883 | 1.8 | 316.2883 | 1.8 | 316.2883 | 1 | 175.7157 | 1 | 175.7157 | 2.6 | 456.8608 | 2.6 | 456.8608 | 3.8 | 667.7197 | 2.5 | 439.2893 | 1.8 | 316.2883 | 1.35 | 237.2162 | 1.35 | 237.2162 | 3.3 | 579.8618 | 2.15 | 377.7888 | 1 | 175.7157 | 1.35 | 237.2162 | 4.9 | 861.0069 | 2.34 | 411.1747 | 1.4625 | 256.9842 | 0.3 | 52.7147 | 0.3 | 52.7147 | 0 | 0 | 0.4 | 70.2863 | 0.2 | 35.1431 | 0.35 | 61.5005
| b) | Moose ACSR
| c) | Twin Disc Iinsulator string with Tension Hardware for Twin Moose on 400KV side
| d) | Single Disc Iinsulator string with suspension Hardware for Twin Moose on 400KV side
| e) | 400KV Bus post insulators
| f) | Tee Clamps Twin Moose to EH-IPS Al Tube 4" - 400kV side
| g) | Tee Clamps Twin Moose to Twin Moose - 400kV side
| h) | PG Clamps
| i) | Spacer Clamps for Twin Moose
| j) | Ground wire and accessories
|  | Sub Total - 4-E | INR Lakhs |  |  | 316.2883 |  | 316.2883 |  | 316.2883 |  | 316.2883 |  | 175.7157 |  | 175.7157 |  | 456.8608 |  | 456.8608 |  | 667.7197 |  | 439.2893 |  | 316.2883 |  | 237.2162 |  | 237.2162 |  | 579.8618 |  | 377.7888 |  | 175.7157 |  | 237.2162 |  | 861.0069 |  | 411.1747 |  | 256.9842 |  | 52.7147 |  | 52.7147 |  | 0 |  | 70.2863 |  | 35.1431 |  | 61.5005
| 4-F | Foundations for 400 kV Towers & Equipment Support structures
| a) | Towers | [40 empty] | 0 | 0
| i | Towers Type 4C1 | No. | 3.019 | 5 | 15.095 | 5 | 15.095 | 5 | 15.095 | 5 | 15.095 | 3 | 9.057 | 3 | 9.057 | 7 | 21.133 | 5 | 15.095 | 13 | 39.247 | 7 | 21.133 | 3 | 9.057 | 3 | 9.057 | 3 | 9.057 | 7 | 21.133 | 5 | 15.095 | 3 | 9.057 | 3 | 9.057 | 18 | 54.342 | 8 | 24.152 | 5 | 15 | 1.5 | 4.5285 | 1.5 | 4.5285 | 0 | 0 | 2 | 6.038 | 0 | 0 | 0 | 0
| ii | Towers Type 4C2 | No. | 3.019 | 8 | 24.152 | 8 | 24.152 | 8 | 24.152 | 8 | 24.152 | 6 | 18.114 | 4 | 12.076 | 8 | 24.152 | 8 | 24.152 | 8 | 24.152 | 8 | 24.152 | 6 | 18.114 | 6 | 18.114 | 4 | 12.076 | 8 | 24.152 | 10 | 30.19 | 6 | 18.114 | 6 | 18.114 | 6 | 18.114 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 12.076 | 0 | 0 | 0 | 0
| iii | Towers Type 4C3 | No. | 3.019 | 16 | 48.304 | 16 | 48.304 | 16 | 48.304 | 16 | 48.304 | 9 | 27.171 | 10 | 30.19 | 24 | 72.4561 | 16 | 48.304 | 33 | 99.6271 | 24 | 72.4561 | 9 | 27.171 | 13 | 39.247 | 10 | 30.19 | 24 | 72.4561 | 19 | 57.361 | 6 | 18.114 | 9 | 27.171 | 62 | 187.1782 | 20 | 60.3801 | 17 | 51 | 6 | 18.114 | 6 | 18.114 | 0 | 0 | 6 | 18.114 | 0 | 0 | 8 | 24.152
| b) | Equipment support structures | [38 empty] | 0 |  | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
| i | Circuit breaker | No. | 1.2579 | 9 | 11.3213 | 9 | 11.3213 | 13 | 16.3529 | 9 | 11.3213 | 8 | 10.0633 | 7 | 8.8054 | 14 | 17.6108 | 11 | 13.8371 | 23 | 28.9321 | 17 | 21.3846 | 7 | 8.8054 | 8 | 10.0633 | 7 | 8.8054 | 17 | 21.3846 | 14 | 17.6108 | 6 | 7.5475 | 8 | 10.0633 | 29 | 36.4796 | 12 | 15.095 | 8 | 10 | 1.5 | 1.8869 | 1.5 | 1.8869 | 0 | 0 | 1.5 | 1.8869 | 1 | 1.2579 | 2.5 | 3.1448
| ii | Isolator | No. | 0.50317 | 24 | 12.076 | 26 | 13.0823 | 28 | 14.0887 | 26 | 13.0823 | 18 | 9.057 | 15 | 7.5475 | 34 | 17.1077 | 33 | 16.6045 | 63 | 31.6995 | 42 | 21.133 | 17 | 8.5538 | 21 | 10.5665 | 17 | 8.5538 | 42 | 21.133 | 34 | 17.1077 | 16 | 8.0507 | 21 | 10.5665 | 72 | 36.228 | 34 | 17.1077 | 23 | 11.5 | 5 | 2.5158 | 4 | 2.0127 | 0 | 0 | 4 | 2.0127 | 1 | 0.50317 | 5 | 2.5158
| iii | CT | No. | 0.10063 | 27 | 2.7171 | 27 | 2.7171 | 30 | 3.019 | 27 | 2.7171 | 18 | 1.8114 | 15 | 1.5095 | 42 | 4.2266 | 27 | 2.7171 | 60 | 6.038 | 51 | 5.1323 | 18 | 1.8114 | 24 | 2.4152 | 12 | 1.2076 | 51 | 5.1323 | 39 | 3.9247 | 18 | 1.8114 | 24 | 2.4152 | 87 | 8.7551 | 45 | 4.5285 | 30 | 3 | 6 | 0.6038 | 6 | 0.6038 | 0 | 0 | 4.5 | 0.45285 | 0 | 0 | 6 | 0.6038
| iv | CVT | No. | 0.10063 | 18 | 1.8114 | 18 | 1.8114 | 18 | 1.8114 | 18 | 1.8114 | 12 | 1.2076 | 12 | 1.2076 | 24 | 2.4152 | 18 | 1.8114 | 33 | 3.3209 | 24 | 2.4152 | 12 | 1.2076 | 12 | 1.2076 | 12 | 1.2076 | 24 | 2.4152 | 18 | 1.8114 | 12 | 1.2076 | 12 | 1.2076 | 42 | 4.2266 | 27 | 2.7171 | 18 | 1.8 | 3 | 0.3019 | 3 | 0.3019 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| v | SA | No. | 0.050317 | 18 | 0.9057 | 18 | 0.9057 | 18 | 0.9057 | 18 | 0.9057 | 18 | 0.9057 | 15 | 0.75475 | 30 | 1.5095 | 24 | 1.2076 | 48 | 2.4152 | 36 | 1.8114 | 15 | 0.75475 | 15 | 0.75475 | 15 | 0.75475 | 36 | 1.8114 | 30 | 1.5095 | 12 | 0.6038 | 21 | 1.0567 | 60 | 3.019 | 30 | 1.5095 | 21 | 1.05 | 6 | 0.3019 | 3 | 0.15095 | 0 | 0 | 3 | 0.15095 | 3 | 0.15095 | 3 | 0.15095
| vi | Line Trap | No. | 0.50317 | 8 | 4.0253 | 8 | 4.0253 | 8 | 4.0253 | 8 | 4.0253 | 4 | 2.0127 | 4 | 2.0127 | 12 | 6.038 | 8 | 4.0253 | 18 | 9.057 | 12 | 6.038 | 4 | 2.0127 | 4 | 2.0127 | 4 | 2.0127 | 12 | 6.038 | 8 | 4.0253 | 4 | 2.0127 | 4 | 2.0127 | 24 | 12.076 | 14 | 7.0443 | 8 | 4 | 2 | 1.0063 | 2 | 1.0063 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| vii | BPI | No. | 0.050317 | 63 | 3.17 | 63 | 3.17 | 63 | 3.17 | 63 | 3.17 | 30 | 1.5095 | 28 | 1.4089 | 99 | 4.9814 | 99 | 4.9814 | 156 | 7.8494 | 99 | 4.9814 | 30 | 1.5095 | 36 | 1.8114 | 30 | 1.5095 | 99 | 4.9814 | 69 | 3.4719 | 30 | 1.5095 | 42 | 2.1133 | 108 | 5.4342 | 90 | 4.5285 | 45 | 2.25 | 12 | 0.6038 | 12 | 0.6038 | 0 | 0 | 30 | 1.5095 | 6 | 0.3019 | 30 | 1.5095
|  | Sub Total - 4-F | INR Lakhs |  |  | 123.5778 |  | 124.5842 |  | 130.9241 |  | 124.5842 |  | 80.9093 |  | 74.5694 |  | 171.6303 |  | 132.7355 |  | 252.3383 |  | 180.637 |  | 78.9972 |  | 95.2495 |  | 75.3744 |  | 180.637 |  | 152.1074 |  | 68.0282 |  | 83.7773 |  | 365.8528 |  | 137.0627 |  | 99.6 |  | 29.863 |  | 29.2088 |  | 0 |  | 42.2409 |  | 2.2139 |  | 32.0769
| 4-G | Erection, Testing & commisioning Charges for 400 kV Outdoor Equipments
| a) | 420 KV Circuit breaker | No. | 0.33427 | 9 | 3.0084 | 11 | 3.677 | 13 | 4.3455 | 11 | 3.677 | 8 | 2.6741 | 7 | 2.3399 | 14 | 4.6798 | 11 | 3.677 | 23 | 7.6882 | 17 | 5.6826 | 7 | 2.3399 | 8 | 2.6741 | 7 | 2.3399 | 17 | 5.6826 | 14 | 4.6798 | 6 | 2.0056 | 8 | 2.6741 | 29 | 9.6938 | 12 | 4.0112 | 8 | 2.6741 | 1.5 | 0.5014 | 1.5 | 0.5014 | 0 | 0 | 1.5 | 0.5014 | 1 | 0.33427 | 2.5 | 0.83567
| b) | 420KV Isolator | No. | 0.22285 | 24 | 5.3483 | 26 | 5.794 | 28 | 6.2397 | 26 | 5.794 | 18 | 4.0112 | 15 | 3.3427 | 34 | 7.5768 | 33 | 7.3539 | 63 | 14.0393 | 42 | 9.3595 | 17 | 3.7884 | 21 | 4.6798 | 17 | 3.7884 | 42 | 9.3595 | 34 | 7.5768 | 16 | 3.5655 | 21 | 4.6798 | 72 | 16.0449 | 34 | 7.5768 | 23 | 5.1254 | 5 | 1.1142 | 4 | 0.89138 | 0 | 0 | 4 | 0.89138 | 1 | 0.22285 | 5 | 1.1142
| c) | 420 KV Current Transformer | No. | 0.066854 | 30 | 2.0056 | 30 | 2.0056 | 30 | 2.0056 | 30 | 2.0056 | 18 | 1.2034 | 15 | 1.0028 | 42 | 2.8079 | 27 | 1.805 | 60 | 4.0112 | 51 | 3.4095 | 18 | 1.2034 | 24 | 1.6045 | 12 | 0.80224 | 48 | 3.209 | 39 | 2.6073 | 18 | 1.2034 | 24 | 1.6045 | 87 | 5.8163 | 45 | 3.0084 | 30 | 2.0056 | 6 | 0.40112 | 4.5 | 0.30084 | 0 | 0 | 4.5 | 0.30084 | 0 | 0 | 6 | 0.40112
| d) | 420KV CVT | No. | 0.066854 | 18 | 1.2034 | 18 | 1.2034 | 18 | 1.2034 | 18 | 1.2034 | 12 | 0.80224 | 12 | 0.80224 | 24 | 1.6045 | 18 | 1.2034 | 33 | 2.2062 | 24 | 1.6045 | 12 | 0.80224 | 12 | 0.80224 | 12 | 0.80224 | 24 | 1.6045 | 18 | 1.2034 | 12 | 0.80224 | 12 | 0.80224 | 42 | 2.8079 | 27 | 1.805 | 18 | 1.2034 | 3 | 0.20056 | 3 | 0.20056 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| e) | 390KV surge Arrestor | No. | 0.033427 | 18 | 0.60168 | 24 | 0.80224 | 30 | 1.0028 | 24 | 0.80224 | 18 | 0.60168 | 15 | 0.5014 | 30 | 1.0028 | 24 | 0.80224 | 48 | 1.6045 | 36 | 1.2034 | 15 | 0.5014 | 15 | 0.5014 | 15 | 0.5014 | 36 | 1.2034 | 30 | 1.0028 | 12 | 0.40112 | 21 | 0.70196 | 60 | 2.0056 | 30 | 1.0028 | 21 | 0.70196 | 6 | 0.20056 | 3 | 0.10028 | 0 | 0 | 15 | 0.5014 | 3 | 0.10028 | 3 | 0.10028
| f) | Towers & Beams - Lattice Type | Set | 7.0196 | 1 | 7.0196 | 1 | 7.0196 | 1 | 7.0196 | 1 | 7.0196 | 0.672 | 4.7172 | 0.623 | 2.9388 | 1.31 | 3.8498 | 0.984 | 3.7882 | 2.03 | 14.2499 | 1.33 | 18.9523 | 0.672 | 12.736 | 0.784 | 9.985 | 0.616 | 6.1508 | 1.553 | 9.5521 | 1.147 | 10.9563 | 0.672 | 7.3626 | 0.768 | 5.6545 | 2.05 | 11.5917 | 1.31 | 15.1851 | 0.81875 | 12.4328 | 0.3 | 3.4775 | 0.25 | 0.86938 | 0 | 0 | 0.3 | 0 | 0.1 | 0 | 0.3 | 0
| g) | Support Structures - Pipe Type | Set | 2.2285 | 1 | 2.2285 | 1 | 2.2285 | 1 | 2.2285 | 1 | 2.2285 | 0.672 | 1.4975 | 0.623 | 1.3883 | 1.31 | 2.9193 | 0.984 | 2.1928 | 2.03 | 4.5238 | 1.33 | 2.9638 | 0.672 | 1.4975 | 0.784 | 1.7471 | 0.616 | 1.3727 | 1.553 | 3.4608 | 1.147 | 2.556 | 0.672 | 1.4975 | 0.768 | 1.7115 | 2.05 | 4.5683 | 1.31 | 2.9193 | 0.81875 | 1.8245 | 0.3 | 0.66854 | 0.25 | 0.55711 | 0 | 0 | 0.3 | 0.66854 | 0.15 | 0.33427 | 0.3 | 0.66854
| h) | Bus Bars formation etc | Set | 16.7134 | 1 | 16.7134 | 1 | 16.7134 | 1 | 16.7134 | 1 | 16.7134 | 0.672 | 11.2314 | 0.623 | 10.4125 | 1.31 | 21.8946 | 0.984 | 16.446 | 2.03 | 33.9282 | 1.33 | 22.2289 | 0.672 | 11.2314 | 0.784 | 13.1033 | 0.616 | 10.2955 | 1.553 | 25.9559 | 1.147 | 19.1703 | 0.672 | 11.2314 | 0.768 | 12.8359 | 2.05 | 34.2625 | 1.31 | 21.8946 | 0.81875 | 13.6841 | 0.3 | 5.014 | 0.25 | 4.1784 | 0 | 0 | 0.3 | 5.014 | 0.1 | 1.6713 | 0.3 | 5.014
| k) | Control & Protection panels | [38 empty] | 0 |  | 0
| i | 400KV CB relay Panel | No. | 0.33427 | 9 | 3.0084 | 11 | 3.677 | 13 | 4.3455 | 11 | 3.677 | 8 | 2.6741 | 7 | 2.3399 | 14 | 4.6798 | 11 | 3.677 | 23 | 7.6882 | 17 | 5.6826 | 7 | 2.3399 | 8 | 2.6741 | 7 | 2.3399 | 17 | 5.6826 | 14 | 4.6798 | 6 | 2.0056 | 8 | 2.6741 | 29 | 9.6938 | 12 | 4.0112 | 8 | 2.6741 | 1.5 | 0.5014 | 1.5 | 0.5014 | 0 | 0 | 0.5 | 0.16713 | 1 | 0.33427 | 2.5 | 0.83567
| ii | 400KV Line Protection Panel | No. | 1.0028 | 4 | 4.0112 | 4 | 4.0112 | 4 | 4.0112 | 4 | 4.0112 | 2 | 2.0056 | 2 | 2.0056 | 6 | 6.0168 | 4 | 4.0112 | 9 | 9.0252 | 6 | 6.0168 | 2 | 2.0056 | 2 | 2.0056 | 2 | 2.0056 | 6 | 6.0168 | 4 | 4.0112 | 2 | 2.0056 | 2 | 2.0056 | 12 | 12.0337 | 7 | 7.0196 | 4 | 4.0112 | 1 | 1.0028 | 1 | 1.0028 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| iii | 400/220/33KV Transformer Protection Panel | No. | 0.60895 | 2 | 1.2179 | 2 | 1.2179 | 2 | 1.2179 | 2 | 1.2179 | 2 | 1.2179 | 1 | 0.60895 | 2 | 1.2179 | 2 | 1.2179 | 2 | 1.2179 | 2 | 1.2179 | 2 | 1.2179 | 2 | 1.2179 | 1 | 0.60895 | 2 | 1.2179 | 3 | 1.8269 | 2 | 1.2179 | 2 | 1.2179 | 2 | 1.2179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.60895 | 0 | 0 | 0 | 0
| iv | 400KV Reactor Protection Panel | No. | 0.10648 | 0 | 0 | 2 | 0.21297 | 4 | 0.42594 | 2 | 0.21297 | 2 | 0.21297 | 2 | 0.21297 | 2 | 0.21297 | 3 | 0.31945 | 5 | 0.53242 | 4 | 0.42594 | 1 | 0.10648 | 1 | 0.10648 | 2 | 0.21297 | 4 | 0.42594 | 3 | 0.31945 | 0 | 0 | 3 | 0.31945 | 6 | 0.63891 | 3 | 0.31945 | 3 | 0.31945 | 1 | 0.10648 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.10648 | 1 | 0.10648
| v | Duplicate Bus Bar Protection Panel - 400KV | No. | 1.781 | 1 | 1.781 | 1 | 1.781 | 1 | 1.781 | 1 | 1.781 | 1 | 1.781 | 1 | 1.781 | 1 | 1.781 | 1 | 1.781 | 1 | 1.781 | 1 | 1.781 | 1 | 1.781 | 1 | 1.781 | 1 | 1.781 | 1 | 1.781 | 1 | 1.781 | 1 | 1.781 | 1 | 1.781 | 1 | 1.781 | 1 | 1.781 | 1 | 1.781 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| l) | PLCC Equipments (Both for 400 kV & 220 kV) | Set | 1.3928 | 1 | 1.3928 | 1 | 1.3928 | 1 | 1.3928 | 1 | 1.3928 | 0.75 | 1.0446 | 0.75 | 1.0446 | 1.25 | 1.741 | 1.4 | 1.9499 | 2.5 | 3.482 | 1.25 | 1.741 | 1 | 1.3928 | 0.75 | 1.0446 | 0.75 | 1.0446 | 1.25 | 1.741 | 1 | 1.3928 | 0.75 | 1.0446 | 0.75 | 1.0446 | 1.15 | 1.6017 | 0.825 | 1.149 | 0.61875 | 0.86179 | 0.25 | 0.3482 | 0.25 | 0.3482 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Sub Total - 4-G | INR Lakhs |  |  | 49.5402 |  | 51.7365 |  | 53.9328 |  | 51.7365 |  | 35.675 |  | 30.7216 |  | 61.9848 |  | 50.225 |  | 105.9779 |  | 82.2697 |  | 42.9438 |  | 43.9272 |  | 34.0461 |  | 76.893 |  | 63.7637 |  | 36.1242 |  | 39.7072 |  | 113.7579 |  | 71.6836 |  | 49.2996 |  | 13.5368 |  | 9.4517 |  | 0 |  | 8.6537 |  | 3.1038 |  | 9.076
|  | Total - 4 | INR Lakhs |  |  | 2185.8151 |  | 2348.6934 |  | 2497.6493 |  | 2326.6534 |  | 1588.0781 |  | 1458.4417 |  | 3086.36 |  | 2573.0805 |  | 4757.6772 |  | 3425.8613 |  | 1687.6228 |  | 1760.5643 |  | 1518.3215 |  | 3556.1315 |  | 2791.5305 |  | 1403.5342 |  | 1767.8322 |  | 6085.0307 |  | 2856.6849 |  | 1945.1441 |  | 392.5678 |  | 358.8179 |  | 0 |  | 370.5772 |  | 139.8734 |  | 350.0336
| 5 | 220 kV Bays & Equipments
| 5-A | 245 kV equipment
| a) | Circuit Breaker 245 kV
| i | 1600 A, 40 kA | No. | 17.3378 | 9 | 156.0406 | 9 | 156.0406 | 9 | 156.0406 | 7 | 121.3649 | 7 | 121.3649 | 7 | 121.3649 | 9 | 156.0406 | 12 | 208.0542 | 15 | 260.0677 | 9 | 156.0406 | 7 | 121.3649 | 7 | 121.3649 | 6 | 104.0271 | 9 | 156.0406 | 10 | 173.3785 | 7 | 121.3649 | 7 | 121.3649 | 8 | 138.7028 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 17.3378 | 1 | 17.3378 | 0 | 0 | 0 | 0
| ii | 2500 A, 40 kA | No. | 17.9053 | 1 | 17.9053 | 1 | 17.9053 | 1 | 17.9053 | 1 | 17.9053 | 1 | 17.9053 | 1 | 17.9053 | 1 | 17.9053 | 1 | 17.9053 | 1 | 17.9053 | 1 | 17.9053 | 1 | 17.9053 | 1 | 17.9053 | 1 | 17.9053 | 1 | 17.9053 | 1 | 17.9053 | 1 | 17.9053 | 1 | 17.9053 | 1 | 17.9053 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) | Current Transformer 245 kV | [38 empty] | 0 |  | 0
| i | 1600 A, 40 kA , 5 core, with 120% extended current | No. | 3.7043 | 27 | 100.0159 | 27 | 100.0159 | 27 | 100.0159 | 21 | 77.7902 | 21 | 77.7902 | 21 | 77.7902 | 27 | 100.0159 | 36 | 133.3546 | 45 | 166.6932 | 27 | 100.0159 | 21 | 77.7902 | 21 | 77.7902 | 18 | 66.6773 | 27 | 100.0159 | 30 | 111.1288 | 21 | 77.7902 | 21 | 77.7902 | 24 | 88.903 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 11.1129 | 3 | 11.1129 | 0 | 0 | 0 | 0
| ii | 1600 A, 40 kA, 5 core, with 150% extended current | No. | 3.9553 | 3 | 11.866 | 3 | 11.866 | 3 | 11.866 | 3 | 11.866 | 3 | 11.866 | 3 | 11.866 | 3 | 11.866 | 3 | 11.866 | 3 | 11.866 | 3 | 11.866 | 3 | 11.866 | 3 | 11.866 | 3 | 11.866 | 3 | 11.866 | 3 | 11.866 | 3 | 11.866 | 3 | 11.866 | 3 | 11.866 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| c) | CVT 245 kV | [38 empty] | 0 |  | 0
| i | 8800 pf, S- Ph, with 3 secondaries | No. | 3.34 | 6 | 20.04 | 6 | 20.04 | 6 | 20.04 | 6 | 20.04 | 6 | 20.04 | 6 | 20.04 | 6 | 20.04 | 6 | 20.04 | 6 | 20.04 | 6 | 20.04 | 6 | 20.04 | 6 | 20.04 | 6 | 20.04 | 6 | 20.04 | 6 | 20.04 | 6 | 20.04 | 6 | 20.04 | 6 | 20.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ii | 4400 pf, S- Ph with 3 secondaries | No. | 3.3359 | 18 | 60.0454 | 18 | 60.0454 | 18 | 60.0454 | 12 | 40.0303 | 12 | 40.0303 | 12 | 40.0303 | 18 | 60.0454 | 30 | 100.0757 | 36 | 120.0908 | 18 | 60.0454 | 12 | 40.0303 | 12 | 40.0303 | 12 | 40.0303 | 18 | 60.0454 | 18 | 60.0454 | 12 | 40.0303 | 12 | 40.0303 | 15 | 50.0378 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 10.0076 | 0 | 0 | 0 | 0 | 0 | 0
| d) | Isolator 245 kV | No. | [37 empty] | 0 |  | 0
| i | 1600A, 40 kA, DB Type with two E/S | No. | 4.5691 | 9 | 41.1219 | 9 | 41.1219 | 9 | 41.1219 | 7 | 31.9837 | 7 | 31.9837 | 7 | 31.9837 | 9 | 41.1219 | 12 | 54.8292 | 15 | 68.5365 | 9 | 41.1219 | 7 | 31.9837 | 7 | 31.9837 | 6 | 27.4146 | 9 | 41.1219 | 10 | 45.691 | 7 | 31.9837 | 7 | 31.9837 | 8 | 36.5528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 4.5691 | 1 | 4.5691 | 0 | 0 | 0 | 0
| ii | 1600A, 40 kA, DB Type with one E/S | No. | 3.8603 | 9 | 34.7424 | 9 | 34.7424 | 9 | 34.7424 | 7 | 27.0219 | 7 | 27.0219 | 7 | 27.0219 | 9 | 34.7424 | 11 | 42.463 | 13 | 50.1835 | 9 | 34.7424 | 7 | 27.0219 | 7 | 27.0219 | 6 | 23.1616 | 9 | 34.7424 | 10 | 38.6027 | 7 | 27.0219 | 7 | 27.0219 | 8 | 30.8822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3.8603 | 1 | 3.8603 | 0 | 0 | 0 | 0
| iii | 1600A, 40 kA, DB, Tandem Type without E/S | No. | 3.4448 | 17 | 58.5608 | 17 | 58.5608 | 17 | 58.5608 | 13 | 44.7818 | 13 | 44.7818 | 13 | 44.7818 | 17 | 58.5608 | 23 | 79.2293 | 29 | 99.8978 | 17 | 58.5608 | 13 | 44.7818 | 13 | 44.7818 | 11 | 37.8923 | 17 | 58.5608 | 19 | 65.4503 | 13 | 44.7818 | 13 | 44.7818 | 15 | 51.6713 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 6.8895 | 2 | 6.8895 | 0 | 0 | 0 | 0
| iv | 2500A, 40 KA, DB Type with Two E/S | No. | 4.8228 | 2 | 9.6456 | 2 | 9.6456 | 2 | 9.6456 | 2 | 9.6456 | 2 | 9.6456 | 2 | 9.6456 | 2 | 9.6456 | 2 | 9.6456 | 2 | 9.6456 | 2 | 9.6456 | 2 | 9.6456 | 2 | 9.6456 | 2 | 9.6456 | 2 | 9.6456 | 2 | 9.6456 | 2 | 9.6456 | 2 | 9.6456 | 2 | 9.6456 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| v | 1600A, 40kA with one E/S, S-phase | No. | 1.7311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 13.8485 | 14 | 24.235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| vi | 1600A, 40 kA without E/S, S phase |  | 1.1722 | [36 empty] | 0 |  | 0
| e) | 216 kV Surge Arrestors | No. | 0.74356 | 24 | 17.8454 | 24 | 17.8454 | 24 | 17.8454 | 18 | 13.384 | 18 | 13.384 | 18 | 13.384 | 24 | 17.8454 | 34 | 25.281 | 49 | 36.4344 | 24 | 17.8454 | 18 | 13.384 | 18 | 13.384 | 15 | 11.1534 | 24 | 17.8454 | 27 | 20.0761 | 18 | 13.384 | 18 | 13.384 | 21 | 15.6147 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 2.2307 | 3 | 2.2307 | 0 | 0 | 0 | 0
|  | Sub Total - 5-A | INR Lakhs |  | 333 | 527.8294 |  | 527.8294 |  | 527.8294 |  | 415.8137 |  | 415.8137 |  | 415.8137 |  | 527.8294 |  | 716.5923 |  | 885.5957 |  | 527.8294 |  | 415.8137 |  | 415.8137 |  | 369.8134 |  | 527.8294 |  | 573.8297 |  | 415.8137 |  | 415.8137 |  | 471.8216 | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 56.0078 |  | 46.0003 |  | 0 |  | 0
| 5-B | 220 kV Simplex type Panels
| a) | Circuit breaker relay panel With Auto reclosure | No. | 8.0229 | 6 | 48.1375 | 6 | 48.1375 | 6 | 48.1375 | 4 | 32.0917 | 4 | 32.0917 | 4 | 32.0917 | 6 | 48.1375 | 10 | 80.2291 | 10 | 80.2291 | 6 | 48.1375 | 4 | 32.0917 | 4 | 32.0917 | 4 | 32.0917 | 6 | 48.1375 | 6 | 48.1375 | 4 | 32.0917 | 4 | 32.0917 | 5 | 40.1146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 8.0229 | 0 | 0 | 0 | 0 | 0 | 0
| b) | Circuit breaker relay panel Without Auto reclosure | No. | 6.4523 | 4 | 25.8092 | 4 | 25.8092 | 4 | 25.8092 | 4 | 25.8092 | 4 | 25.8092 | 4 | 25.8092 | 4 | 25.8092 | 3 | 19.3569 | 4 | 25.8092 | 4 | 25.8092 | 4 | 25.8092 | 4 | 25.8092 | 3 | 19.3569 | 4 | 25.8092 | 5 | 32.2615 | 4 | 25.8092 | 4 | 25.8092 | 4 | 25.8092 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 6.4523 | 0 | 0 | 0 | 0
| c) | Line protection panel | No. | 18.1825 | 6 | 109.0949 | 6 | 109.0949 | 6 | 109.0949 | 4 | 72.7299 | 4 | 72.7299 | 4 | 72.7299 | 6 | 109.0949 | 10 | 181.8248 | 10 | 181.8248 | 6 | 109.0949 | 4 | 72.7299 | 4 | 72.7299 | 4 | 72.7299 | 6 | 109.0949 | 6 | 109.0949 | 4 | 72.7299 | 4 | 72.7299 | 5 | 90.9124 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 18.1825 | 0 | 0 | 0 | 0 | 0 | 0
| d) | Single Bus Bar protection panel | No. | 63.4584 | 1 | 63.4584 | 1 | 63.4584 | 1 | 63.4584 | 1 | 63.4584 | 1 | 63.4584 | 1 | 63.4584 | 1 | 63.4584 | 1 | 63.4584 | 1 | 63.4584 | 1 | 63.4584 | 1 | 63.4584 | 1 | 63.4584 | 1 | 63.4584 | 1 | 63.4584 | 1 | 63.4584 | 1 | 63.4584 | 1 | 63.4584 | 1 | 63.4584 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Sub Total - 5-B | INR Lakhs |  |  | 246.5 |  | 246.5 |  | 246.5 |  | 194.0892 |  | 194.0892 |  | 194.0892 |  | 246.5 |  | 344.8693 |  | 351.3215 |  | 246.5 |  | 194.0892 |  | 194.0892 |  | 187.6369 |  | 246.5 |  | 252.9522 |  | 194.0892 |  | 194.0892 |  | 220.2946 | [5 empty] | 0 |  | 0 |  | 26.2054 |  | 6.4523 |  | 0 |  | 0
| 5-C | 220 kV Towers, Beams & Support structures
| a) | Tower Type 2C1 - Number * Unit Weight | MT | 0.68144 | 67.5 | 45.997 | 67.5 | 45.997 | 67.5 | 45.997 | 54 | 36.7976 | 54 | 36.7976 | 54 | 36.7976 | 67.5 | 45.997 | 121.5 | 82.7946 | 121.5 | 82.7946 | 67.5 | 45.997 | 54 | 36.7976 | 54 | 36.7976 | 54 | 36.7976 | 67.5 | 45.997 | 67.5 | 45.997 | 54 | 36.7976 | 54 | 36.7976 | 67.5 | 45.997 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| b) | Tower Type 2C2 - Number * Unit Weight | MT | 0.68144 | 72 | 49.0635 | 72 | 49.0635 | 72 | 49.0635 | 60 | 40.8862 | 60 | 40.8862 | 60 | 40.8862 | 72 | 49.0635 | 48 | 32.709 | 48 | 32.709 | 72 | 49.0635 | 60 | 40.8862 | 60 | 40.8862 | 60 | 40.8862 | 72 | 49.0635 | 68 | 46.3377 | 60 | 40.8862 | 60 | 40.8862 | 72 | 49.0635 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 5.4515 | 6 | 4.0886 | 0 | 0 | 0 | 0
| c) | Tower Type 2C3 - Number * Unit Weight | MT | 0.68144 | 14 | 9.5401 | 14 | 9.5401 | 14 | 9.5401 | 10.5 | 7.1551 | 10.5 | 7.1551 | 10.5 | 7.1551 | 14 | 9.5401 | 56 | 38.1605 | 63 | 42.9305 | 14 | 9.5401 | 10.5 | 7.1551 | 10.5 | 7.1551 | 10.5 | 7.1551 | 14 | 9.5401 | 14 | 9.5401 | 10.5 | 7.1551 | 10.5 | 7.1551 | 10.5 | 7.1551 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 9.5401 | 0 | 0 | 0 | 0
| d) | Beam Type 2B1 - Number * Unit Weight | MT | 0.68144 | 30 | 20.4431 | 30 | 20.4431 | 30 | 20.4431 | 24 | 16.3545 | 24 | 16.3545 | 24 | 16.3545 | 30 | 20.4431 | 48 | 32.709 | 48 | 32.709 | 30 | 20.4431 | 24 | 16.3545 | 24 | 16.3545 | 24 | 16.3545 | 30 | 20.4431 | 30 | 20.4431 | 24 | 16.3545 | 24 | 16.3545 | 30 | 20.4431 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| e) | Beam Type 2B2 - Number * Unit Weight | MT | 0.68144 | 42.5 | 28.9611 | 42.5 | 28.9611 | 42.5 | 28.9611 | 32.5 | 22.1467 | 32.5 | 22.1467 | 37.5 | 25.5539 | 42.5 | 28.9611 | 27.5 | 18.7395 | 32.5 | 22.1467 | 42.5 | 28.9611 | 32.5 | 22.1467 | 32.5 | 22.1467 | 32.5 | 22.1467 | 42.5 | 28.9611 | 42.5 | 28.9611 | 32.5 | 22.1467 | 32.5 | 22.1467 | 47.5 | 32.3683 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5 | 1.7036 | 5 | 3.4072 | 0 | 0 | 0 | 0
| f) | Beam Type 2B3 - Number * Unit Weight | MT | 0.68144 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| g) | Equipment Support Structure - Number * Unit Weight | MT | 0.68144 | 33 | 22.4874 | 33 | 22.4874 | 33 | 22.4874 | 24 | 16.3545 | 24 | 16.3545 | 24 | 16.3545 | 33 | 22.4874 | 49.5 | 33.7311 | 51 | 34.7533 | 27 | 18.3988 | 24 | 16.3545 | 24 | 16.3545 | 22.5 | 15.3323 | 33 | 22.4874 | 34.5 | 23.5096 | 24 | 16.3545 | 24 | 16.3545 | 31.5 | 21.4653 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.5 | 3.0665 | 1.5 | 1.0222 | 0 | 0 | 0 | 0
|  | Sub Total - 5-C | INR Lakhs |  |  | 176.4922 |  | 176.4922 |  | 176.4922 |  | 139.6946 |  | 139.6946 |  | 143.1018 |  | 176.4922 |  | 238.8437 |  | 248.0431 |  | 172.4036 |  | 139.6946 |  | 139.6946 |  | 138.6725 |  | 176.4922 |  | 174.7886 |  | 139.6946 |  | 139.6946 |  | 176.4922 | [5 empty] | 0 |  | 0 |  | 10.2216 |  | 18.0581 |  | 0 |  | 0
| 5-D | 220 KVTubular type (Pipe) Equipment support / mounting Structures
| a) | CVT - Number * Unit Weight | MT | 0.90858 | 12 | 10.903 | 12 | 10.903 | 12 | 10.903 | 9 | 8.1772 | 9 | 8.1772 | 9 | 8.1772 | 12 | 10.903 | 18 | 16.3545 | 16.5 | 14.9916 | 12 | 10.903 | 9 | 8.1772 | 9 | 8.1772 | 9 | 8.1772 | 12 | 10.903 | 12 | 10.903 | 9 | 8.1772 | 9 | 8.1772 | 10.5 | 9.5401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5 | 1.3629 | 0 | 0 | 0 | 0 | 0 | 0
| b) | BPI - Number * Unit Weight | MT | 0.90858 | 34 | 30.8918 | 34 | 30.8918 | 34 | 30.8918 | 24 | 21.806 | 24 | 24 | 22.5 | 20.4431 | 34 | 30.8918 | 42 | 38.1605 | 45 | 40.8862 | 34 | 30.8918 | 24 | 21.806 | 24 | 21.806 | 21 | 19.0802 | 34 | 30.8918 | 30 | 27.2575 | 24 | 21.806 | 24 | 21.806 | 27 | 24.5317 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5 | 3.18 | 3.5 | 3.18 | 0 | 0 | 0 | 0
| c) | Isolators - Number * Unit Weight | MT | 0.90858 | 55.5 | 50.4263 | 55.5 | 50.4263 | 55.5 | 50.4263 | 27 | 27 | 27 | 24.5317 | 43.5 | 39.5234 | 55.5 | 50.4263 | 84 | 76.321 | 97.5 | 88.5868 | 55.5 | 50.4263 | 27 | 24.5317 | 27 | 24.5317 | 23 | 20.8974 | 55.5 | 50.4263 | 61.5 | 55.8778 | 27 | 24.5317 | 27 | 24.5317 | 49.5 | 44.9749 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 5.4515 | 6 | 5.4515 | 0 | 0 | 0 | 0
| d) | SA - Number * Unit Weight | MT | 0.90858 | 12 | 10.903 | 12 | 10.903 | 12 | 10.903 | 9 | 8.1772 | 9 | 8.1772 | 9 | 8.1772 | 12 | 10.903 | 18 | 16.3545 | 18 | 16.3545 | 12 | 10.903 | 9 | 8.1772 | 9 | 8.1772 | 7.5 | 6.8144 | 12 | 10.903 | 13.5 | 12.2659 | 9 | 8.1772 | 9 | 8.1772 | 10.5 | 9.5401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5 | 1.3629 | 1.5 | 1.3629 | 0 | 0 | 0 | 0
|  | Sub Total - 5-D | INR Lakhs |  |  | 103.1242 |  | 103.1242 |  | 103.1242 |  | 65.1605 |  | 64.8862 |  | 76.321 |  | 103.1242 |  | 147.1904 |  | 160.8192 |  | 103.1242 |  | 62.6922 |  | 62.6922 |  | 54.9693 |  | 103.1242 |  | 106.3042 |  | 62.6922 |  | 62.6922 |  | 88.5868 | [5 empty] | 0 |  | 0 |  | 11.3573 |  | 9.9944 |  | 0 |  | 0
| 5-E | Bus Bar & Hard ware materials for 220 kV
| a) | Quad Disc Iinsulator string with Tension Hardware for Quad Moose (220KV Main Bus) | Set | 197.6802 | 1.5 | 296.5202 | 1.5 | 296.5202 | 1.5 | 296.5202 | 1 | 197.6802 | 1 | 197.6802 | 1 | 197.6802 | 1.5 | 296.5202 | 3.25 | 642.4605 | 3.5 | 691.8806 | 1.5 | 296.5202 | 1 | 197.6802 | 1 | 197.6802 | 1 | 197.6802 | 1.5 | 296.5202 | 1.5 | 296.5202 | 1 | 197.6802 | 1 | 197.6802 | 1.25 | 247.1002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 49.42 | 0.25 | 49.42 | 0 | 0 | 0 | 0
| b) | Twin Disc Iinsulator string with Suspension Hardware for Quad Moose(220KV Main Bus) | Set
| c) | Twin Disc Iinsulator string with Tension Hardware for Twin Moose (220KV Transfer Bus and Jack Bus) | Set
| d) | Twin Disc Iinsulator string with Suspension Hardware for Twin Moose(220KV Transfer and Jack Bus) | Set
| e) | 220KV Bus post I nsulators | No.
| f) | 4" EH-IPS Alluminium Tube(OD- 114.2, ID-97.18) | Metre
| g) | Moose ACSR | Metre
| h) | Tee Clamps Quad Moose to Twin Moose | No.
| i) | Tee Clamps Twin Moose to Twin Moose - 220kv side | No.
| j) | Tee Clamps Twin Moose to 4' IPS Al Tube - 220kv side | No.
| k) | Spacer Clamps for Quad Moose ACSR | No.
| l) | Spacer Clamps for Twin Moose ACSR | No.
| m) | PG Clamps | No.
| n) | Ground wire with Accessories | Lump Sum
|  | Sub Total - 5-E | INR Lakhs |  |  | 296.5202 |  | 296.5202 |  | 296.5202 |  | 197.6802 |  | 197.6802 |  | 197.6802 |  | 296.5202 |  | 642.4605 |  | 691.8806 |  | 296.5202 |  | 197.6802 |  | 197.6802 |  | 197.6802 |  | 296.5202 |  | 296.5202 |  | 197.6802 |  | 197.6802 |  | 247.1002 |  | 0 |  |  |  | 0 |  | 0 |  | 49.42 |  | 49.42 |  | 0 |  | 0
| 5-F | Foundations for 220 kV Towers & Equipment mounting structures
| a) | Towers
| i | Towers Type 2C1 | No. | 2.5158 | 15 | 37.7375 | 15 | 37.7375 | 15 | 37.7375 | 12 | 30.19 | 12 | 30.19 | 12 | 30.19 | 15 | 37.7375 | 27 | 67.9276 | 27 | 67.9276 | 15 | 37.7375 | 12 | 30.19 | 12 | 30.19 | 12 | 30.19 | 15 | 37.7375 | 15 | 37.7375 | 12 | 30.19 | 12 | 30.19 | 15 | 37.7375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ii | Towers Type 2C2 | No. | 2.5158 | 18 | 45.285 | 18 | 45.285 | 18 | 45.285 | 15 | 37.7375 | 15 | 37.7375 | 15 | 37.7375 | 18 | 45.285 | 12 | 30.19 | 12 | 30.19 | 18 | 45.285 | 15 | 37.7375 | 15 | 37.7375 | 15 | 37.7375 | 18 | 45.285 | 17 | 42.7692 | 15 | 37.7375 | 15 | 37.7375 | 18 | 45.285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 5.0317 | 2 | 5.0317 | 0 | 0 | 0 | 0
| iii | Towers Type 2C3 | No. | 2.5158 | 4 | 10.0633 | 4 | 10.0633 | 4 | 10.0633 | 3 | 7.5475 | 3 | 7.5475 | 3 | 7.5475 | 4 | 10.0633 | 16 | 40.2534 | 18 | 45.285 | 4 | 10.0633 | 3 | 7.5475 | 3 | 7.5475 | 3 | 7.5475 | 4 | 10.0633 | 4 | 10.0633 | 3 | 7.5475 | 3 | 7.5475 | 3 | 7.5475 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 5.0317 | 0 | 0 | 0 | 0
| b) | Equipment support structures | [21 empty] | 0 | [16 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| i | Circuit breakers | No. | 0.50317 | 10 | 5.0317 | 10 | 5.0317 | 10 | 5.0317 | 8 | 4.0253 | 8 | 4.0253 | 8 | 4.0253 | 10 | 5.0317 | 13 | 6.5412 | 14 | 7.0443 | 10 | 5.0317 | 8 | 4.0253 | 8 | 4.0253 | 7 | 3.5222 | 10 | 5.0317 | 11 | 5.5348 | 8 | 4.0253 | 8 | 4.0253 | 9 | 4.5285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.50317 | 1 | 0.50317 | 0 | 0 | 0 | 0
| ii | Isolators | No. | 0.40253 | 37 | 14.8937 | 37 | 14.8937 | 37 | 14.8937 | 29 | 11.6735 | 29 | 11.6735 | 29 | 11.6735 | 37 | 14.8937 | 56 | 22.5419 | 65 | 26.1647 | 37 | 14.8937 | 29 | 11.6735 | 29 | 11.6735 | 25 | 10.0633 | 37 | 14.8937 | 41 | 16.5039 | 29 | 11.6735 | 29 | 11.6735 | 33 | 13.2836 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 1.6101 | 4 | 1.6101 | 0 | 0 | 0 | 0
| iii | C.Ts | No. | 0.10063 | 30 | 3.019 | 30 | 3.019 | 30 | 3.019 | 24 | 2.4152 | 24 | 2.4152 | 24 | 2.4152 | 30 | 3.019 | 39 | 3.9247 | 42 | 4.2266 | 30 | 3.019 | 24 | 2.4152 | 24 | 2.4152 | 21 | 2.1133 | 30 | 3.019 | 33 | 3.3209 | 24 | 2.4152 | 24 | 2.4152 | 27 | 2.7171 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0.3019 | 3 | 0.3019 | 0 | 0 | 0 | 0
| iv | CVT | No. | 0.10063 | 24 | 2.4152 | 24 | 2.4152 | 24 | 2.4152 | 18 | 1.8114 | 18 | 1.8114 | 18 | 1.8114 | 24 | 2.4152 | 36 | 3.6228 | 33 | 3.3209 | 24 | 2.4152 | 18 | 1.8114 | 18 | 1.8114 | 18 | 1.8114 | 24 | 2.4152 | 24 | 2.4152 | 18 | 1.8114 | 18 | 1.8114 | 21 | 2.1133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0.3019 | 0 | 0 | 0 | 0 | 0 | 0
| v | SA | No. | 0.40253 | 24 | 9.6608 | 24 | 9.6608 | 24 | 9.6608 | 18 | 7.2456 | 18 | 7.2456 | 18 | 7.2456 | 24 | 9.6608 | 36 | 14.4912 | 36 | 14.4912 | 24 | 9.6608 | 18 | 7.2456 | 18 | 7.2456 | 15 | 6.038 | 24 | 9.6608 | 27 | 10.8684 | 18 | 7.2456 | 18 | 7.2456 | 21 | 8.4532 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 1.2076 | 3 | 1.2076 | 0 | 0 | 0 | 0
| vi | WT | No. | 0.50317 | 12 | 6.038 | 12 | 6.038 | 12 | 6.038 | 8 | 4.0253 | 8 | 4.0253 | 8 | 4.0253 | 12 | 6.038 | 20 | 10.0633 | 20 | 10.0633 | 12 | 6.038 | 8 | 4.0253 | 8 | 4.0253 | 8 | 4.0253 | 12 | 6.038 | 12 | 6.038 | 8 | 4.0253 | 8 | 4.0253 | 10 | 5.0317 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1.0063 | 0 | 0 | 0 | 0 | 0 | 0
| vii | BPI | No. | 0.40253 | 68 | 27.3723 | 68 | 27.3723 | 68 | 27.3723 | 48 | 19.3216 | 48 | 19.3216 | 45 | 18.114 | 68 | 27.3723 | 84 | 33.8128 | 90 | 36.228 | 68 | 27.3723 | 48 | 19.3216 | 48 | 19.3216 | 45 | 18.114 | 68 | 27.3723 | 60 | 24.152 | 48 | 19.3216 | 48 | 19.3216 | 54 | 21.7368 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 2.8177 | 7 | 2.8177 | 0 | 0 | 0 | 0
|  | Sub Total - 5-F | INR Lakhs |  |  | 161.5166 |  | 161.5166 |  | 161.5166 |  | 125.993 |  | 125.993 |  | 124.7854 |  | 161.5166 |  | 233.3689 |  | 244.9417 |  | 161.5166 |  | 125.993 |  | 125.993 |  | 121.1626 |  | 161.5166 |  | 159.4033 |  | 125.993 |  | 125.993 |  | 148.4343 | [5 empty] | 0 |  | 0 |  | 12.7804 |  | 16.5039 |  | 0 |  | 0
| 5-G | Erection Testing & commissioning Charges 220 kV
OUTDOOR EQUIPMENTS
| a) | 245 KV Circuit breakers | No. | 0.22285 | 10 | 2.2285 | 10 | 2.2285 | 10 | 2.2285 | 8 | 1.7828 | 8 | 1.7828 | 8 | 1.7828 | 10 | 2.2285 | 13 | 2.897 | 14 | 3.1198 | 10 | 2.2285 | 8 | 1.7828 | 8 | 1.7828 | 7 | 1.5599 | 10 | 2.2285 | 11 | 2.4513 | 8 | 1.7828 | 8 | 1.7828 | 9 | 2.0056 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.22285 | 1 | 0.22285 | 0 | 0 | 0 | 0
| b) | 245 KV Isolators | No. | 0.16713 | 37 | 6.184 | 37 | 6.184 | 37 | 6.184 | 29 | 4.8469 | 29 | 4.8469 | 29 | 4.8469 | 37 | 6.184 | 56 | 9.3595 | 65 | 10.8637 | 37 | 6.184 | 29 | 4.8469 | 29 | 4.8469 | 25 | 4.1784 | 37 | 6.184 | 41 | 6.8525 | 29 | 4.8469 | 29 | 4.8469 | 33 | 5.5154 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0.66854 | 4 | 0.66854 | 0 | 0 | 0 | 0
| c) | 245 KV Current Transformers | No. | 0.055711 | 30 | 1.6713 | 30 | 1.6713 | 30 | 1.6713 | 24 | 1.3371 | 24 | 1.3371 | 24 | 1.3371 | 30 | 1.6713 | 39 | 2.1727 | 42 | 2.3399 | 30 | 1.6713 | 24 | 1.3371 | 24 | 1.3371 | 21 | 1.1699 | 30 | 1.6713 | 33 | 1.8385 | 24 | 1.3371 | 24 | 1.3371 | 27 | 1.5042 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0.16713 | 3 | 0.16713 | 0 | 0 | 0 | 0
| d) | 245 KV CVT | No. | 0.055711 | 24 | 1.3371 | 24 | 1.3371 | 24 | 1.3371 | 18 | 1.0028 | 18 | 1.0028 | 18 | 1.0028 | 24 | 1.3371 | 36 | 2.0056 | 36 | 2.0056 | 24 | 1.3371 | 18 | 1.0028 | 18 | 1.0028 | 18 | 1.0028 | 24 | 1.3371 | 24 | 1.3371 | 18 | 1.0028 | 18 | 1.0028 | 21 | 1.1699 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0.16713 | 0 | 0 | 0 | 0 | 0 | 0
| e) | 216 KV surge Arrestors | No. | 0.033427 | 24 | 0.80224 | 24 | 0.80224 | 24 | 0.80224 | 18 | 0.60168 | 18 | 0.60168 | 18 | 0.60168 | 24 | 0.80224 | 33 | 1.1031 | 36 | 1.2034 | 24 | 0.80224 | 18 | 0.60168 | 18 | 0.60168 | 15 | 0.5014 | 24 | 0.80224 | 27 | 0.90252 | 18 | 0.60168 | 18 | 0.60168 | 21 | 0.70196 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0.10028 | 3 | 0.10028 | 0 | 0 | 0 | 0
| f) | 220 kV Towers , Beams | Set | 6.6854 | 1 | 6.6854 | 1 | 6.6854 | 1 | 6.6854 | 0.8 | 5.3483 | 0.8 | 5.3483 | 0.8 | 5.3483 | 1 | 6.6854 | 1.32 | 8.8247 | 1.41 | 9.4264 | 1 | 6.6854 | 0.8 | 5.3483 | 0.8 | 5.3483 | 0.8 | 5.3483 | 1 | 6.6854 | 1 | 6.6854 | 0.8 | 5.3483 | 0.8 | 5.3483 | 1 | 6.6854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 1.3371 | 0.2 | 1.3371 | 0 | 0 | 0 | 0
| g) | 221 kV Tubular type Pipe Structures | Set | 3.3427 | 1 | 3.3427 | 1 | 3.3427 | 1 | 3.3427 | 0.8 | 2.6741 | 0.8 | 2.6741 | 0.8 | 2.6741 | 1 | 3.3427 | 1.32 | 4.4123 | 1.41 | 4.7132 | 1 | 3.3427 | 0.8 | 2.6741 | 0.8 | 2.6741 | 0.8 | 2.6741 | 1 | 3.3427 | 1 | 3.3427 | 0.8 | 2.6741 | 0.8 | 2.6741 | 1 | 3.3427 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.66854 | 0.2 | 0.66854 | 0 | 0 | 0 | 0
| h) | 220 kV Bus Bars formation etc | Set | 17.8277 | 1 | 17.8277 | 1 | 17.8277 | 1 | 17.8277 | 0.8 | 14.2621 | 0.8 | 14.2621 | 0.8 | 14.2621 | 1 | 17.8277 | 1.32 | 23.5325 | 1.41 | 25.137 | 1 | 17.8277 | 0.8 | 14.2621 | 0.8 | 14.2621 | 0.8 | 14.2621 | 1 | 17.8277 | 1 | 17.8277 | 0.8 | 14.2621 | 0.8 | 14.2621 | 1 | 17.8277 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 3.5655 | 0.2 | 3.5655 | 0 | 0 | 0 | 0
| j) | Control & Protection panels | [6 empty] | 1 | [31 empty] | 0 |  | 0
| i | Circuit breaker relay panel | No. | 0.27856 | 10 | 2.7856 | 10 | 2.7856 | 6 | 1.6713 | 8 | 2.2285 | 8 | 2.2285 | 8 | 2.2285 | 10 | 2.7856 | 13 | 3.6212 | 14 | 3.8998 | 10 | 2.7856 | 8 | 2.2285 | 8 | 2.2285 | 7 | 1.9499 | 10 | 2.7856 | 11 | 3.0641 | 8 | 2.2285 | 8 | 2.2285 | 9 | 2.507 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.27856 | 0 | 0 | 0 | 0 | 0 | 0
| ii | Line protection panel | No. | 0.73539 | 6 | 4.4123 | 6 | 4.4123 | 6 | 4.4123 | 4 | 2.9416 | 4 | 2.9416 | 4 | 2.9416 | 6 | 4.4123 | 10 | 7.3539 | 10 | 7.3539 | 6 | 4.4123 | 4 | 2.9416 | 4 | 2.9416 | 4 | 2.9416 | 6 | 4.4123 | 6 | 4.4123 | 4 | 2.9416 | 4 | 2.9416 | 5 | 3.677 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.73539 | 0 | 0 | 0 | 0 | 0 | 0
| iii | Single Bus Bar protection panel | No. | 2.2285 | 1 | 2.2285 | 1 | 2.2285 | 1 | 2.2285 | 1 | 2.2285 | 1 | 2.2285 | 1 | 2.2285 | 1 | 2.2285 | 1 | 2.2285 | 1 | 2.2285 | 1 | 2.2285 | 1 | 2.2285 | 1 | 2.2285 | 1 | 2.2285 | 1 | 2.2285 | 1 | 2.2285 | 1 | 2.2285 | 1 | 2.2285 | 1 | 2.2285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Sub Total - 5-G | INR Lakhs |  |  | 49.5052 |  | 49.5052 |  | 48.3909 |  | 39.2543 |  | 39.2543 |  | 39.2543 |  | 49.5052 |  | 67.5111 |  | 72.2911 |  | 49.5052 |  | 39.2543 |  | 39.2543 |  | 37.8169 |  | 49.5052 |  | 50.9425 |  | 39.2543 |  | 39.2543 |  | 47.1653 |  | 0 |  |  |  | 0 |  | 0 |  | 7.911 |  | 6.7299 |  | 0 |  | 0
|  | Total - 5 | INR Lakhs |  |  | 1561.4878 |  | 1561.4878 |  | 1560.3735 |  | 1177.6854 |  | 1177.4112 |  | 1191.0455 |  | 1561.4878 |  | 2390.8362 |  | 2654.893 |  | 1557.3991 |  | 1175.2172 |  | 1175.2172 |  | 1107.7517 |  | 1561.4878 |  | 1614.7408 |  | 1175.2172 |  | 1175.2172 |  | 1399.8949 |  | 0 |  |  |  | 0 |  | 0 |  | 173.9036 |  | 153.1589 |  | 0 |  | 0
| 6 | Hard cost ---- Grand total (1+2+3+4+5) | INR Lakhs |  |  | 7154.3059 |  | 8178.5815 |  | 9146.7931 |  | 7641.7398 |  | 6800.2827 |  | 5728.7423 |  | 9074.9976 |  | 10183.0111 |  | 15796.4319 |  | 10267.9196 |  | 6511.7025 |  | 6595.1406 |  | 5697.3878 |  | 12356.6318 |  | 10069.4108 |  | 5765.733 |  | 7359.1828 |  | 14384.2995 | 0 | 5360.6198 | 0 | 4364.3576 |  | 848.2878 |  | 416.1857 |  | 204.2068 |  | 1525.9684 |  | 577.0988 |  | 787.0078
|  | Material and Equipment Cost Only |  |  |  | 6181.6703 |  | 7156.9974 |  | 8100.1394 |  | 6675.5484 |  | 5947.0853 |  | 4913.8819 |  | 7948.9549 |  | 8919.4131 |  | 14119.8324 |  | 9068.3979 |  | 5665.6981 |  | 5737.9834 |  | 4877.3753 |  | 11036.7588 |  | 8955.4318 |  | 4957.1279 |  | 6476.9226 |  | 12721.7024 |  | 4610.2753 |  | 3705.6478 |  | 780.6861 |  | 375.0827 |  | 181.074 |  | 1416.7923 |  | 548.659 |  | 721.653
|  | Taxes |  | 12.51% |  | 773.0797 | 0 | 895.0541 | 0 | 1013.0034 | 0 | 834.8441 | 0 | 743.7425 | 0 | 614.5301 | 0 | 994.0963 | 0 | 1115.4618 | 0 | 1765.8262 | 0 | 1134.0938 | 0 | 708.5522 | 0 | 717.5922 | 0 | 609.9646 | 0 | 1380.2571 | 0 | 1119.9663 | 0 | 619.9384 | 0 | 810.0039 | 0 | 1590.9761 |  | 576.561 | 0 | 463.4283 | 0 | 97.6326 | 0 | 46.9078 | 0 | 22.6451 | 0 | 177.184 | 0 | 68.6153 | 0 | 90.2499
| 7 | Total Cost Including Taxes |  |  |  | 7927.3856 | 0 | 9073.6356 | 0 | 10159.7966 | 0 | 8476.5839 | 0 | 7544.0252 | 0 | 6343.2723 | 0 | 10069.0939 | 0 | 11298.4729 | 0 | 17562.2581 | 0 | 11402.0134 | 0 | 7220.2547 | 0 | 7312.7328 | 0 | 6307.3524 | 0 | 13736.8889 | 0 | 11189.3771 | 0 | 6385.6715 | 0 | 8169.1867 | 0 | 15975.2756 |  | 5937.1809 | 0 | 4827.7859 | 0 | 945.9204 | 0 | 463.0936 | 0 | 226.8519 | 0 | 1703.1524 | 0 | 645.7141 | 0 | 877.2577
[18 empty] | 5728.74 | 9075 | 10183.01 | 15796.43 | 10267.92
Note on B200: Author:

## Summary (hidden)
CERC
Capital Cost Benchmarking
Summary of Costs
Alternates
| Particulars | Unit | Alt - 1 | Alt - 2 | Alt - 3 | Alt - 4 | Alt - 5 | Alt - 6 | Alt - 7 | Alt - 8 | Alt - 9 | Alt - 10 | Alt - 11 | Alt - 12 | Alt - 13 | Alt - 14 | Alt - 15 | Alt - 16 | Alt - 17 | Alt - 18 | Alt - 19 | Alt - 20
| Total Hard Cost | INR Lakhs | 7154.3059 | 8178.5815 | 9146.7931 | 7641.7398 | 6800.2827 | 5728.7423 | 9074.9976 | 10183.0111 | 15796.4319 | 10267.9196 | 6511.7025 | 6595.1406 | 5697.3878 | 12356.6318 | 10069.4108 | 5765.733 | 7359.1828 | 14384.2995 | 5360.6198 | 4364.3576
| Total Hard Cost | INR Crore | 71.5431 | 81.7858 | 91.4679 | 76.4174 | 68.0028 | 57.2874 | 90.75 | 101.8301 | 157.9643 | 102.6792 | 65.117 | 65.9514 | 56.9739 | 123.5663 | 100.6941 | 57.6573 | 73.5918 | 143.843 | 53.6062 | 43.6436
Combinations
| Particulars | Unit | Combination-1 | Combination-2 | Combination-3 | Combination-4 | Combination-5 | Combination-6
| Total Hard Cost | INR Lakhs | 848.2878 | 416.1857 | 204.2068 | 1525.9684 | 577.0988 | 787.0078
| Total Hard Cost | INR Crore | 8.4829 | 4.1619 | 2.0421 | 15.2597 | 5.771 | 7.8701