## Annexure-III 1 to 3
Annexure-III
SH 1/3
Pro-forma for furnishing Actual annual performance/operational data for the Hydro Electric generating stations for the 5-year period from 2012-13 to 2016-17
| Particulars |  | Units | 2012-13 | 2013-14 | 2014-15 | 2015-16 | 2016-17
1 | Name of Company |  |  | NHPC TLD
2 | Name of Station |  |  | BAIRASIUL POWER STATION
3 | Installed Capacity and Configuration |  | (MW) | 180 MW
4 | Station Location |  | Under ground or Surface | Surface
5 | Type of Excitation System |  |  | Static
6 | Live Storage Capacity |  | (Million Cubic) | 0.725 M | 0.725 M | 0.725 M | 0.725 M | 0.725 M
7 | Rated Head |  | Metres | 240 M | 240 M | 240 M | 240 M | 240 M
8 | Head at Full Reservoir Level (FRL) |  | Metres | 282.21 M | 282.21 M | 282.21 M | 282.21 M | 282.21 M
9 | Head at Minimum Draw down Level (MDDL) |  | Metres | 275.80 M | 275.80 M | 275.80 M | 275.80 M | 275.80 M
10 | MW Capability at FRL |  | MW | 180 | 180 | 180 | 180 | 180
11 | MW Capability at MDDL |  | MW | 175.9 | 175.9 | 175.9 | 175.9 | 175.9
12 | Cost of spares :
12.1 | Cost of spares capitalized in books of accounts |  | (Rs. Lakhs) | 422.4654 | 253.0002 | 928.5055 | 87.2224 | 97.3799
12.2 | Cost of spares included in the capital cost for the purpose of tariff |  | (Rs. Lakhs) | NIL | NIL | NIL | NIL | NIL
Period
13 | Generation :
13.1 | Actual Gross Generation at Generator Terminals |  | (MU) | 721.56 | 638.07 | 796.6925 | 745.591 | 669.2033
13.2 | Actual Net Generation Ex-bus including free power |  | (MU) | 707.93 | 626.4509 | 779.2657 | 732.3349 | 662.3755
13.3 | Scheduled generation Ex-bus including free power |  | (MU) | 706.8102 | 626.2042 | 755.8258 | 709.0342 | 640.8877
14 | Actual Auxiliary Energy Consumption excluding colony consumption |  | (MU) | 13.63 | 12.5996 | 18.3001 | 13.2173 | 7.2735
15 | Actual Energy supplied to Colony from the station |  | (MU) | NIL | NIL | NIL | NIL | NIL
16 | Average Declared Capacity (DC) during the year |  | (MW) | 175.14 | 166.71 | 156.92 | 165.95 | 166.26
Annexure-III
SH 2/3
| Period |  | Units | 2012-13 | 2013-14 | 2014-15 | 2015-16 | 2016-17
17 | Weighted Average duration of outages ( Unit-wise details)
17.1 | Scheduled outages |  | (Days) | 32.1264 | 83.5826 | 69.2079 | 66.4896 | 72.7896
17.2 | Forced outages |  | (Days) | 18.9071 | 23.8771 | 38.6368 | 17.4521 | 13.2194
18 | Cost of spares actually consumed |  | (Rs. Lakhs) | 157.1816 | 142.7846 | 265.9351 | 904.0978 | 233.0853
19 | Average stock of spares |  | (Rs. Lakhs) | 456.8069 | 759.1122 | 1216.0516 | 1566.2298 | 1928.0144
Month wise Design Energy (Existing)
Month |  | Period | Design Energy as approved by CEA (MU) |  | Month | Period | Design Energy as approved by CEA (MU)
April |  | 1-10 | 30.5 |  | October | 1-10 | 12.91 |  |  | 1291 | 540
|  | 11-20 | 33.63 | 33.63 |  | 11-20 | 11.14 | 11.14 |  | 1114 | 540
|  | 21-30 | 33.72 | 33.72 |  | 21-31 | 11.34 | 11.34 |  | 1134 | 540
May |  | 1-10 | 35.15 | 35.15 | November | 1-10 | 9.12 | 9.12 |  | 912 | 540
|  | 11-20 | 32.63 | 32.63 |  | 11-20 | 8.33 | 8.33 |  | 833 | 540
|  | 21-31 | 38.22 | 38.22 |  | 21-30 | 7.77 | 7.77 |  | 777 | 540
June |  | 1-10 | 31.84 | 31.84 | December | 1-10 | 7.05 | 7.05 |  | 705 | 540
|  | 11-20 | 30.35 | 30.35 |  | 11-20 | 7.11 | 7.11 |  | 711 | 540
|  | 21-30 | 30.61 | 30.61 |  | 21-31 | 8.05 | 8.05 |  | 805 | 540
July |  | 1-10 | 32.13 | 32.13 | January | 1-10 | 7.47 | 7.47 |  | 747 | 540
|  | 11-20 | 35.61 | 35.61 |  | 11-20 | 7.84 | 7.84 |  | 784 | 540
|  | 21-31 | 41.5 | 41.5 |  | 21-31 | 8.5 | 8.5 |  | 850 | 540
August |  | 1-10 | 40.89 | 40.89 | February | 1-10 | 8.57 | 8.57 |  | 857 | 540
|  | 11-20 | 37.57 | 37.57 |  | 11-20 | 10.28 | 10.28 |  | 1028 | 540
|  | 21-31 | 36.62 | 36.62 |  | 21-28 | 10.58 | 10.58 |  | 1058 | 540
September |  | 1-10 | 23.6 | 23.6 | March | 1-10 | 16.28 | 16.28 |  | 1628 | 540
|  | 11-20 | 19.69 | 19.69 |  | 11-20 | 18.81 | 18.81 |  | 1881 | 540
|  | 21-30 | 16.57 | 16.57 |  | 21-31 | 27.3 | 27.3 |  | 2730 | 540
[5 empty] | Total |  | 779.28
Storage Hydro plants shall also furnish actual monthly average peaking generation in MW achieved during the period 2012-13 to 2016-17 against the monthly average peaking capability approved by CEA as per following format:
Month |  | Expected Avg. of daily 3-hour peaking capacity as approved by CEA |  |  | Actual monthly average of daily 3-hour peaking (MW) for the period 2012-13 to 2016-17
April |  | 178.2 |  |  | 168.1122 |  |  |  | 178.2 | 1% | 180
May |  | 178.2 |  |  | 179.7935 |  |  |  | 178.2 | 1% | 180
June |  | 178.2 |  |  | 178.5027 |  |  |  | 178.2 | 1% | 180
July |  | 178.2 |  |  | 175.9099 |  |  |  | 178.2 | 1% | 180
August |  | 178.2 |  |  | 175.6242 |  |  |  | 178.2 | 1% | 180
September |  | 178.2 |  |  | 161.3221 |  |  |  | 178.2 | 1% | 180
October |  | 178.2 |  |  | 166.6993 |  |  |  | 178.2 | 1% | 180
November |  | 178.2 |  |  | 160.6682 |  |  |  | 178.2 | 1% | 180
December |  | 178.2 |  |  | 154.5372 |  |  |  | 178.2 | 1% | 180
January |  | 178.2 |  |  | 125.0708 |  |  |  | 178.2 | 1% | 180
February |  | 178.2 |  |  | 169.8244 |  |  |  | 178.2 | 1% | 180
March |  | 178.2 |  |  | 177.9161 |  |  |  | 178.2 | 1% | 180
Annexure III
SH 3/3
1 | List of beneficiaries/customers along with allocation by GoI including (allocation of unallocated share) / capacity as contracted should also be furnished separately for each generating station.
2 | Declared Capacity should be as per Regulation 31(3) of CERC Tariff Regulations for the period 2014-19 including month wise information may be furnished.
3 | Any relevant point or a specific fact having bearing on performance or operating parameters may also be highlighted or brought to the notice of the Commission.
Month wise Design Energy (Post R&M)
Month |  | Period | Design Energy as approved by CEA (MU) |  | Month | Period | Design Energy as approved by CEA (MU)
April |  | 1-10 | 17.25 |  | October | 1-10 | 14.66 |  |  | 1466 | 540
|  | 11-20 | 23.22 | 23.22 |  | 11-20 | 13.39 | 13.39 |  | 1339 | 540
|  | 21-30 | 30.23 | 30.23 |  | 21-31 | 13.38 | 13.38 |  | 1338 | 540
May |  | 1-10 | 26.84 | 26.84 | November | 1-10 | 10.47 | 10.47 |  | 1047 | 540
|  | 11-20 | 25.46 | 25.46 |  | 11-20 | 9.19 | 9.19 |  | 919 | 540
|  | 21-31 | 23.83 | 23.83 |  | 21-30 | 8.63 | 8.63 |  | 863 | 540
June |  | 1-10 | 28.56 | 28.56 | December | 1-10 | 7.71 | 7.71 |  | 771 | 540
|  | 11-20 | 30.13 | 30.13 |  | 11-20 | 7.4 | 7.4 |  | 740 | 540
|  | 21-30 | 37.21 | 37.21 |  | 21-31 | 7.75 | 7.75 |  | 775 | 540
July |  | 1-10 | 34.56 | 34.56 | January | 1-10 | 6.69 | 6.69 |  | 669 | 540
|  | 11-20 | 36.96 | 36.96 |  | 11-20 | 6.02 | 6.02 |  | 602 | 540
|  | 21-31 | 45.144 | 45.144 |  | 21-31 | 7.55 | 7.55 |  | 755 | 540
August |  | 1-10 | 41.04 | 41.04 | February | 1-10 | 6.86 | 6.86 |  | 686 | 540
|  | 11-20 | 41.04 | 41.04 |  | 11-20 | 6.48 | 6.48 |  | 648 | 540
|  | 21-31 | 37.24 | 37.24 |  | 21-28 | 5.34 | 5.34 |  | 534 | 540
September |  | 1-10 | 28.31 | 28.31 | March | 1-10 | 6.53 | 6.53 |  | 653 | 540
|  | 11-20 | 21.42 | 21.42 |  | 11-20 | 6.94 | 6.94 |  | 694 | 540
|  | 21-30 | 19.1 | 19.1 |  | 21-31 | 16.07 | 16.07 |  | 1607 | 540
[5 empty] | Total |  | 708.604
Note:
CEA vide its Letter No. 13/2(NHPC)/HE&RM/2015/923 date25/08/2015 has approved Design Energy of 708.59 MU. CERC in its Order dated 03/06/2016 has agreed for Design Energy of 708.59 MU subject to Model Study as suggested by CEA.

## Annexure-IV
Annexure –IV
PLANT AVAILABILITY/SCHEDULED PLANT LOAD FACTOR ACHIEVED Generating company: NHPC LTD. Name of Generating station: Bairasiul Power Station Installed Capacity (MW) : 180 MW Normative Annual Plant Availability Factor (%) approved by Commission : 90%
Plant Availability Factor Achieved (%)
Month | 2012-13 | 2013-14 | 2014-15 | 2015-16 | 2016-17 | Reasons for shortfall in PAF achieved vis-a-vis NAPAF
April | 101.5152 | 102.1324 | 76.3187 | 89.5965 | 102.1324 | DURING 2014-15: LESS PAF DUE TO OUTAGE OF U#2 FOR PROBLEM IN THURST BEARING PAD (22/3/2014 - 06/04/2014) & STATOR EARTH FAULT (12/04/2014 - 04/05/2014) AND COMPLETE SHUTDOWN OF POWER HOUSE FOR RESERVOIR FLUSHING THROUGH DT GATE FROM 14/09/2014 TO 21/09/2014 . | 168.1122
May | 102.1324 | 102.1324 | 97.5707 | 100.5032 | 102.1324 |  | 179.7935
June | 102.1324 | 100.7856 | 100.6809 | 102.1324 | 95.1178 |  | 178.5027
July | 102.1324 | 100.4489 | 94.4924 | 97.6626 | 98.8378 |  | 175.9099
August | 98.2063 | 100.4489 | 99.4287 | 99.58 | 95.1088 |  | 175.6242
September | 84.193 | 101.6274 | 64.0731 | 100.6173 | 102.1324 |  | 161.3221
October | 97.1867 | 86.9266 | 81.0362 | 100.4489 | 102.1324 |  | 166.6993
November | 91.6947 | 102.1324 | 84.725 | 86.5881 | 85.6684 |  | 160.6682
December | 93.7149 | 102.1324 | 90.431 | 74.1407 | 73.187 |  | 154.5372
January | 102.1324 | 32.1132 | 67.6717 | 73.712 | 75.2987 |  | 125.0708
February | 102.1324 | 98.5249 | 100.1261 | 90.4253 | 85.2908 |  | 169.8244
March | 102.1324 | 92.3573 | 100.4489 | 102.1324 | 102.1324 |  | 177.9161
Annual | 98.2809 | 93.349 | 88.0573 | 93.1255 | 93.297
Plant Load Factor Achieved (%)
Month | 2012-13 | 2013-14 | 2014-15 | 2015-16 | 2016-17 | Reasons for shortfall in PLF achieved vis-a-vis Target PLF
April
May
June
July |  | Not Applicable
August
September
October
November
December
January
February
March
Annual

## Annexure-XIX
Annexure-XIX
Name of the Utility |  | NHPC LTD.
Name of the Generating Station |  | Bairasiul Power Station
Station/ Stage/ Unit |  | 3x60 MW
Fuel Type (Coal/ Lignite/ Gas/ Liquid Fuel/ Nuclear/ Hydro | [7 empty] | Hydro
Capacity of Plant (MW) |  | 180 MW
COD |  | 1982-04-01
|  | 2004-05 | 2005-06 | 2006-07 | 2007-08 | 2008-09 | 2009-10 | 2010-11 | 2011-12 | 2012-13 | 2013-14 | 2014-15 | 2015-16 | 2016-17
1 | Plant Availability Factor (PAF) (%) | 94.716 | 95.21 | 94.2205 | 94.9339 | 93.14 | 91.1018 | 94.9949 | 94.9146 | 98.2809 | 93.349 | 88.0573 | 93.1255 | 93.2969
2 | Plant Load Factors (PLF) (%)
3 | Scheduled Energy (MU) | 672.2101 | 771.1986 | 684.4696 | 592.2321 | 667.9174 | 612.253 | 698.667 | 715.6792 | 706.8102 | 626.2042 | 755.8258 | 709.0342 | 640.8877
4 | Scheduled Generation (MU)
5 | Actual Generation (MU) | 689.68 | 790.99 | 698.37 | 609.306 | 673.07 | 622.86 | 711 | 730.5872 | 721.56 | 638.07 | 796.6925 | 745.591 | 669.2033
6 | Quantum of coal consumption (MT) | 1982-04-01 2004-05: Not Applicable
7 | Value of coal (Rs. Lakh)
8 | Specific Coal Consumption (kg/kwh)
9 | Gross Calorific Value of Coal (Kcal/ Kg)
10 | Heat Contribution of Coal (Kcal/ kwh)
11 | Cost Of Specific Coal Consumption (Rs./Kwh) – Finally admitted by CERC
12 | Quantum of Oil Consumption (Lit.)
13 | Value of Oil (Rs. lakh)
14 | Gross calorific value of oil (kcal/lit)
15 | Specific Oil Consumption (ml/ kwh)
16 | Cost Of Specific Oil Consumption (Rs./Kwh) – Finally admitted by CERC
17 | Heat Contribution of Oil (Kcal/ kwh)
18 | Station Heat Rate (kcal/kwh)
19 | Auxiliary Energy Consumption (%) | 1.85 | 1.77 | 1.13 | 1.32 | 1.22 | 1.52 | 1.55 | 1.81 | 1.99 | 1.87 | 2.3 | 1.77 | 1.09
20 | Debt at the end of the year (Rs. Crore) ^ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
21 | Equity (Rs. Crore) | 78.7486 | 78.7471 | 78.8896 | 79.0966 | 79.1828 | 79.2458 | 79.3301 | 79.4874 | 80.7213 | 81.3471 | 84.5622 | 86.9505 | 87.0621
22 | Working Capital (Rs. Crore) – finally admitted by CERC | 16.7851 | 16.1944 | 16.8551 | 17.5534 | 18.2824 | 29.1151 | 30.4981 | 31.9705 | 33.2065 | 35.1896 | 40.1532 | 42.6778 | 45.335
23 | Capital cost (Rs. Crore) – finally admitted by CERC | 180.5451 | 180.5403 | 181.0151 | 181.7053 | 181.9926 | 182.0774 | 182.3586 | 182.8829 | 186.9959 | 189.0817 | 199.7987 | 207.7597 | 208.1319
24 | Capacity Charges/ Annual Fixed Cost (AFC)
(a) Return on equity – pre tax (admitted by CERC)
| Absolute value | 11.0369 | 11.0247 | 11.0346 | 11.059 | 11.0796 | 18.6047 | 18.4027 | 18.2195 | 15.7717 | 16.9167 | 17.3176 | 17.9025 | 18.1634
| Rate (%) * | 14% | 14% | 14% | 14% | 14% | 23.48% | 23.21% | 22.94% | 19.38% | 19.61% | 20.88% | 20.88% | 20.88%
(b) interest on Loan
| Absolute value | 1.6495 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Rate (%) – Weighted Average Rate | 0.125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
(c) Depreciation (finally allowed by CERC)
| Absolute value | 10.2202 | 4.7404 | 4.7826 | 4.8387 | 4.88 | 7.4153 | 7.4459 | 7.5087 | 7.9444 | 8.6478 | 9.4707 | 9.8259 | 10.3619
| Rate (%) | 1982-04-01 2009-10: As the power Station has already completed 12 years, remaining depreciation is uniformily distributed over the balance useful life.
(d) Interest on working Capital
| Absolute value | 1.7205 | 1.6599 | 1.7276 | 1.7992 | 1.8739 | 3.5666 | 3.736 | 3.9164 | 4.0678 | 4.3107 | 5.4207 | 5.7615 | 6.1202
| Rate (%) | 10.25% | 10.25% | 10.25% | 10.25% | 10.25% | 12.25% | 12.25% | 12.25% | 12.25% | 12.25% | 13.5% | 13.5% | 13.5%
(e) Operation and maintenance cost (finally admitted by CERC)
| Absolute value | 30.08 | 31.28 | 32.53 | 33.83 | 35.18 | 60.4599 | 63.9182 | 67.5743 | 71.4396 | 75.5259 | 86.9625 | 92.7403 | 98.9019
Rate (%)
(f) Compensation Allowances | bar: 1982-04-01 2004-05
25 | AFC (Rs. Crore) | 54.7071 | 48.705 | 50.0748 | 51.5269 | 53.0135 | 90.0465 | 93.5028 | 97.2189 | 99.2235 | 105.4011 | 119.1715 | 126.2302 | 133.5474 | 678.9087
26 | Energy Charge (Rs./Kwh) | 0.4029 | 0.3587 | 0.36879 | 0.37948 | 0.39043 | 0.66317 | 0.68863 | 0.71599 | 0.73076 | 0.77625 | 0.87767 | 0.92966 | 0.98354
27 | Total tariff (Rs. Kwh) | 0.80581 | 0.7174 | 0.73758 | 0.75897 | 0.78086 | 1.3263 | 1.3773 | 1.432 | 1.4615 | 1.5525 | 1.7553 | 1.8593 | 1.9671
28 | Revenue realisation before tax (Rs. Crore) | 50.2806 | 56.5757 | 71.6242 | 60.2846 | 61.4818 | 82.2983 | 104.1084 | 132.9115 | 150.9145 | 115.2068 | 118.5844 | 162.1956 | 134.8482
29 | Revenue realisation after tax (Rs. Crore) #
30 | Profit/ loss before tax (Rs. Crore) | 7.0366 | 15.635 | 31.1491 | 10.1345 | -8.8973 | 6.5345 | 27.8633 | 35.9737 | 71.0174 | 21.6737 | 19.5073 | 62.9703 | 14.9008
31 | DSM Generation (MU) | 5.0584 | 6.2813 | 6.4804 | 8.3894 | -2.8049 | 1.8901 | 1.7179 | 2.245 | 0.70854 | 0.062272 | 23.1824 | 22.8426 | 21.0782
32 | DSM Rate (Ps/Kwh)
33 | Revenue from DSM (Rs. Crore) |  |  | 3.07 | 4.64 | 6.73 | 6.53 | 10.9206 | 0.72155 | 15.2708 | 8.776 | 7.6825 | 5.6653 | 5.2666
Note:
1. The data at Sl No. 20 to 27 has been filled based on CERC orders dated 17.06.2015, 18.12.2009 & 14.10.2009
2. The capital cost sl no. 23 & equity at sl no. 21 has been considered as closing equity & capital cost respectively as on 31st March of respective year.
3. The depreciation at Sl No. 24(c) for the period 2004-09 is inclusive of Advance Against Depreciation (AAD)
4. * The Return On Equity (ROE) at Sl No. 24(a) for the period 2004-09 is exclusive of Tax as the same was not part of AFC & separately reimbursable from beneficiaries.
5. ^ The Normative debt at the end of the year (sl no.20) has been considered as ZERO as the grosss normative loan is fully repaid & allowed depreciation in respectve years are more than 70% of admitted additional capitalization.
6. # NHPC calculate Corporate Tax as a whole after considering all the admissible deductions, exemptions etc. as per Income Tax Act. Therefore unitwise calculation has not been made.
Generating Companies are required to submit data for all generating stations.
This is a general format. Plants of different fuel users have to fill the cells as applicable to them. Tariff for the Hydro may be understood as composite tariff.
The data provided for the corresponding years need to mention as Actual or provisional.
Data for each Unit and Stage is required to be submitted in additional sheets as per the format.

## 16-17 vs 15-16
DETAILS OF OPERATION AND MAINTENANCE EXPENSES
Name of the Company : National Hydroelectric Power Corporation Ltd
| Name of Power Station: | BAIRASUIL POWER STATION
Sl. No. | ITEMS | 2015-16 | 2016-17 | Variance % | 13-14 vs 12-13 | 14-15 vs 13-14 | 15-16 vs 14-15 | 16-17 vs 15-16
| 1 | [6 empty] | Reasons for variance
(A) | Breakup of O&M Expenses
1 | Consumption of stores & spares | 90409781 | 23308532 | -74.219 | Minor | Increase is due to carrying out of capital maintenance during current period which was not done in previous period. Under-mentioned items have been issued during current period for capital maintenance work:- i) Consumption of capital spares like Centralised bus bar-13.67 lacs, guide vanes-Rs 27.52 lacs, upper and lower labryinth moving ring- Rs.40.57 lacs. ii) Turbine Oil by Rs 25.01 lacs in comparison to previous period. iii) Temperature signalling device for Rs 7.10 lacs. iv) And other miscellaneous items like Diesel for Rs. 3.18 lac, lower bush for Rs 2.52 lac,SF6 gas cylinder for 2.52 lac,winding set for Rs.2.23 lac, Impeller, Shell and tube heat exchanger etc. | The varience is due to a number of capital spares utilised which are non retribable (Rs. 95 lacs.)during this F.Y 2015-16 as compared to F.Y 2014-15. | Due to consumption of capital spare throuh replacement of transformer in FY 2015-16
|  | 0 | 0
2 | Repair & Maintenance | 0 | 0
2.1 | For Dam,Intake,WCS,De-silting chamber | 38487252 | 30250685 | -21.4008 | 1. Increase is due to repair of Thrust Bearing Mirror disc of 60MW Francis trubine for Rs 13.11 lacs and repair of Spherical valve for Rs 14.17 lacs in this year which was not required in last year. 2. Increase is due to carrying out the work of "Providing and lying of premix carpeting on Dargala Siul Road" for Rs 1.20 crore and other special repair work of Bhaledh weir for Rs 0.66 crore which was not done last year. | Increase is due to taking up the following works which were not undertaken during previous period :- i) Repair of tail pool area of right bank of Power plant building etc. = Rs 15.60 lacs. ii) Repair of BSPS Central School Building= Rs 6.02 lacs. iii) Water proofing treatment of roof slab of machine hall &canteen building at Power House for Rs.17.11 lacs iv) Antitermite treatment of field hostel for Rs.4.58 v) Providing assistants for day to day operation and maintenance of service in hospital for Rs.5.37. vi) Providing of tiles in guest house for Rs 9.23 lacs and other works like fencing of power house building for Rs .3.89 lacs and other miscellaneous works. Further Increase is due to carrying out of following works in capital maintenance which were not done during previous period i) HPVOF coating of under water components of Power House for Rs.23.46 lacs ii) Vibration Analysis and Dynamic Balancing of all the three generatic Units for Rs. 10.24 lacs iii) Re-babbiting of turbine guide bearning pads for Rs.3.38 lacs iv) Repairing of SS liner and lower ring for Rs.28.88 lacs. v) Repairs of stay vanes of 02 nos generating units for Rs. 8 lacs. vi) Increase in repair work of mechanical and mechanical maintenance in comparison to previous period is Rs 19.20 lacs & Rs 20 lacs respectively. And Increase in expenditure is due to taking up the works of R&M of Road, bridges, Dam and reservoir like repair of toe wall, spillway glacies, protection of hill slope, repair of damaged boulder crate by Rs 196.91 lacs, carrying out of various tests from IIT Roorkee for Rs 15.63 lacs, Repair of service gate for Rs 38.29 lacs, R&M electric works like repair of line from Bhaledh weir to Tissa dam site etc by Rs 26.46 lacs and other misc works for Rs 3.02 lacs and also not taking up the work of premix carpet on Dhargala siul road for Rs 112.15 lac during current period. | Minor
2.2 | For Power House and all other works | 69367034 | 89355061 | 28.8149 |  |  |  | The difference is due to award of new work relating to painting of field hostel at surangani during the year for Rs. 18 lakh & painting work for Rs. 13 lakh relating to VIP Guest house. However no such work was awarded during last year. The increase in expenses is also due to HVOF coating of under water component for Rs. 8 lakh and Replacement of SS liner of top cover and lower ring for Rs. 18 lakh. Rs. 3 lakh has been expended for repair of 245 KV type SS6 circuit breaker has been made during the period .
| Sub-Total (Repair and Maintenance) | 107854286 | 119605746 | 10.8957
|  | 0 | 0
3 | Insurance | 41158746 | 41987207 | 2.0128 | As per advices received from Corporate Office. | As per advices received from Corporate Office. | The Insurance policy is being taken by C.O for CPM & Mega Insurance (Rs. 4.17 Cr.) as compared to P.Y Rs. 3.03 Cr.)of the power station & third party insurance policy.
4 | Security Expenses | 76467143 | 96022856 | 25.574 | Minor | Minor | Increase in exp is due to booking of less amount of Security exp in last year. In April & May 2014, as the CISF staff was deputed on Election duty. And increase in DA @ 13% as compared to previous year & amount of 7th pay arrear of central govt employee as per C.O circular no: 479 dt: 13.04.2016. | Increase in exp is due to increase in DA @ 13% as compared to previous year & 7th pay revision of central govt. employee w.e.f. 01.01.2016.
|  | 0 | 0
5 | Administrative Expenses | 0 | 0
5.1 | Rent | 6259734 | 7375842 | 17.83 | Increase is due to receipt of lease rent advice from ED office Banikhet for Rs 11.18 lacs and also deployment of 2 Nos Bolero this year. | Minor |  | As per actual hiring charges of vehicle hired. 3 more Nos. vehicles hired during the Current year as compared to P.Y 2015-16.
5.2 | Electricity charges | 26476732 | 28712434 | 8.444 | Minor | Minor | Minor
5.3 | Travelling & Conveyance | 4716155 | 4215575 | -10.6142 | Minor | The increase in expenditure is due to revision in the rates (more than double) of TA/DA with effect from 01.04.2014 vide Corporate office Circular no 15/2014 dated 02.04.2014 & as per actual tour & travelling of employees. |  | AS per Actual
5.4 | Telephone, Telex & Postage (Communication) | 3880800 | 4225005 | 8.8694 | Increase is due to accountal of liabilties towards Statellite communication expenses(V-SAT) for the year 2013-14 and payment of lease line rent of 4MBPS line to BSNL as compare to last year. |  | Minor
5.5 | Advertisement | 6174711 | 4026669 | -34.7877 | Increase is due to publishing of more press tender as compared to last year. |  | The increase in exp is due to more nos. e-tender for the C.Y as compared to P.Y 2014-15. | Expenditure towards tendering of RMU packages HM & EM works was incurred by C.O for an amount of Rs. 60 lakh ,however only 38 lakh in this regard has been incurred during the year.
5.6 | Donation | 0 | 0
5.7 | Entertainment | 12000 | 14250 | 18.75 | Minor | Minor expense. | Minor expense. | Minor expense.
|  | 0 | 0
| Sub-total (Administrative expenses) | 47520132 | 48569775
6 | Employee Cost | 0 | 0
6.1a | Salaries,wages & allow. -Project | 394988629 | 520811821 | 31.8549 | Central Payroll | Central Payroll | Central Payroll | Provision of wage revision due to 3rd PRC and due to change in ceiling of Gratuity from 10 lacs to 20 lacs
6.2 | Staff welfare expenses | 13420076 | 19417973 | 44.6935 | Due to increase in retired employees medical benefit actuarial valuation provision as compare to last year. | Minor | Minor veriance.The decrease in exp is due to less amount of REHS actuarial valuation advice rec from C.O as compared to previous year. | Due to increase in retired employees medical benefit actuarial valuation provision as compare to last year.
6.3 | Productivity Linked incentive | 19959536 | 51742994 | 159.2395 | Central Payroll | Central Payroll | Central Payroll | Increase due to payment of arear of PLGI at revised rate from F.Y 2010-11 to F.Y 2013-14 and provision of PLGI for Q4 of FY 2016-17 made on revised pay
6.4 | VRS-Ex-gratia | 493596 | 0 | -100 | Central Payroll | Central Payroll | Central Payroll | As per actual no employees opted VRS
6.5 | Ex-gratia | 0 | 0
6.6 | Performance related pay (PRP) | 15460605 | 19959700 | 29.1004 | Central Payroll | Central Payroll | Central Payroll | Incresed due to 1. Normal increase in salary as compared to previous year. 2. Provision made on revised pay for Q4 (F.Y 2016-17)
| Sub-total (Employee Cost) | 444322442 | 611932488
7 | Loss of Store | 2622 | 0
|  | 0 | 0
|  | 0 | 0
9.1 | Allocation of CO Office expenses | 12172799 | 37545725 | 208.4395 | As per advices received | As per advices received | As per advices received | As per advices received
|  | 0 | 0
10 | Others (Specify items) | 12146888 | 13603417 | 11.991 | Increase is due to R&M of field hostel/ Guest House and due to training expenses. | Minor | Minor | Increase is due to purchase of printing & stationery, Training Exps and maintenance exps of guest house & hospital.
11 | Total (1 to 10) | 832054839 | 992575746
12 | Revenue /Recoveries | 26166580 | 38840641 | 48.4361 |  |  |  | Due to Increase in Provision/Liability not required written back and other income.
13 | Net Expenses | 805888259 | 953735105
14 | Capital spares consumed not included in A(1) above and not claimed/allowed by commission for capitalisation

## 15-16 vs 14-15
DETAILS OF OPERATION AND MAINTENANCE EXPENSES
Name of the Company : National Hydroelectric Power Corporation Ltd
| Name of Power Station: | BAIRASUIL POWER STATION
Sl. No. | ITEMS | 2014-15 | 2015-16 | 15-16 vs 14-15 | 15-16 vs 14-15
| 1 |  |  |  | Reasons for variance
(A) | Breakup of O&M Expenses
1 | Consumption of stores & spares | 26593507 | 90409781 | 239.9694 | Due to consumption of capital spare throuh replacement of transformer in FY 2015-16
|  | 0 | 0
2 | Repair & Maintenance | 0 | 0
2.1 | For Dam,Intake,WCS,De-silting chamber | 43616122 | 38487252 | -11.7591 | Decrease is due to taking up the following works in last year i.e., Repair of residential building including laying of tiles and repair of tail pool area of right bank of power plant building & repair cost of sewerage system of surgani colony.
2.2 | For Power House and all other works | 72231729 | 69367034 | -3.966
| Sub-Total (Repair and Maintenance) | 115847851 | 107854286 | -6.9001
|  | 0 | 0
3 | Insurance | 30049774 | 41158746 | 36.9686 | In case of Mega Insurance Police 1. Increase in premium rates on account of deteriorating claim ratio as a result of loss due Fire incident at Uri-II Power Station and submergence of Chutak power Station in November 2014 and June 2015 respectively and other claims during policy period 2014-15 2. Increase in sum-insured due to increase in reinstatement cost of assets on Valuation. 3. Increase in the rate of Service Tax and WCT from 12.36% to 14% and 10.5% to 12.6% respectively. In case of CPM policy, Increase in Sum insured due to valuation of Assets, additional Construction equipment purchased and increase in premium rates & Service Tax/WCT rates as above.
4 | Security Expenses | 67665422 | 76467143 | 13.0077 | Increase in exp is due to booking of less amount of Security exp in last year. In April & May 2014, as the CISF staff was deputed on Election duty. And increase in DA @ 13% as compared to previous year & amount of 7th pay arrear of central govt employee as per C.O circular no: 479 dt: 13.04.2016.
|  | 0 | 0
5 | Administrative Expenses | 0 | 0
5.1 | Rent | 5246784 | 6259734 | 19.3061
5.2 | Electricity charges | 26474264 | 26476732 | 0.0093223
5.3 | Travelling & Conveyance | 6501541 | 4716155 | -27.461
5.4 | Telephone, Telex & Postage (Communication) | 3751401 | 3880800 | 3.4494
5.5 | Advertisement | 1778965 | 6174711 | 247.0957 | The increase in exp is due to more nos. e-tender for the C.Y as compared to P.Y 2014-15.
5.6 | Donation | 0 | 0
5.7 | Entertainment | 6750 | 12000 | 77.7778 | Minor expense.
|  | 0 | 0
| Sub-total (Administrative expenses) | 43759705 | 47520132
6 | Employee Cost | 0 | 0
6.1a | Salaries,wages & allow. -Project | 456745566 | 394988629 | -13.5211
6.2 | Staff welfare expenses | 35565814 | 13420076 | -62.2669 | Decrease in exp due to less amount of REHS actuarial valuation provision as compared to previous year.
6.3 | Productivity Linked incentive | 21166993 | 19959536 | -5.7044
6.4 | VRS-Ex-gratia | 2442898 | 493596 | -79.7947 | As per actual no employees opted VRS
6.5 | Ex-gratia | 0 | 0
6.6 | Performance related pay (PRP) | 13971814 | 15460605 | 10.6557 | Due to normal increase in Salary
| Sub-total (Employee Cost) | 529893085 | 444322442
7 | Loss of Store | 1798 | 2622
|  | 0 | 0
|  | 0 | 0
9.1 | Allocation of CO Office expenses | 19897079 | 12172799 | -38.8212 | As per advices received
|  | 0 | 0
10 | Others (Specify items) | 12337999 | 12146888 | -1.549
11 | Total (1 to 10) | 846046220 | 832054839
12 | Revenue /Recoveries | 22138109 | 26166580 | 18.197 | Due to Increase other income.
13 | Net Expenses | 823908111 | 805888259
14 | Capital spares consumed not included in A(1) above and not claimed/allowed by commission for capitalisation

## 14-15 vs 13-14
DETAILS OF OPERATION AND MAINTENANCE EXPENSES
Name of the Company : National Hydroelectric Power Corporation Ltd
| Name of Power Station: | BAIRASUIL POWER STATION
Sl. No. | ITEMS | 2013-14 | 2014-15 | 14-15 vs 13-14 | 14-15 vs 13-14
| 1 |  |  |  | Reasons for variance
(A) | Breakup of O&M Expenses
1 | Consumption of stores & spares | 14278463 | 26593507 | 86.2491 | Increase is due to carrying out of capital maintenance during current period which was not done in previous period. Under-mentioned items have been issued during current period for capital maintenance work:- i) Consumption of capital spares like Centralised bus bar-13.67 lacs, guide vanes-Rs 27.52 lacs, upper and lower labryinth moving ring- Rs.40.57 lacs. ii) Turbine Oil by Rs 25.01 lacs in comparison to previous period. iii) Temperature signalling device for Rs 7.10 lacs. iv) And other miscellaneous items like Diesel for Rs. 3.18 lac, lower bush for Rs 2.52 lac,SF6 gas cylinder for 2.52 lac,winding set for Rs.2.23 lac, Impeller, Shell and tube heat exchanger etc.
|  | 0 | 0
2 | Repair & Maintenance | 0 | 0
2.1 | For Dam,Intake,WCS,De-silting chamber | 23689073 | 43616122 | 84.1192 | Increase is due to taking up the following works which were not undertaken during previous period :- i) Repair of tail pool area of right bank of Power plant building etc. = Rs 15.60 lacs. ii) Repair of BSPS Central School Building= Rs 6.02 lacs. iii) Water proofing treatment of roof slab of machine hall &canteen building at Power House for Rs.17.11 lacs iv) Antitermite treatment of field hostel for Rs.4.58 v) Providing assistants for day to day operation and maintenance of service in hospital for Rs.5.37. vi) Providing of tiles in guest house for Rs 9.23 lacs and other works like fencing of power house building for Rs .3.89 lacs and other miscellaneous works. Further Increase is due to carrying out of following works in capital maintenance which were not done during previous period i) HPVOF coating of under water components of Power House for Rs.23.46 lacs ii) Vibration Analysis and Dynamic Balancing of all the three generatic Units for Rs. 10.24 lacs iii) Re-babbiting of turbine guide bearning pads for Rs.3.38 lacs iv) Repairing of SS liner and lower ring for Rs.28.88 lacs. v) Repairs of stay vanes of 02 nos generating units for Rs. 8 lacs. vi) Increase in repair work of mechanical and mechanical maintenance in comparison to previous period is Rs 19.20 lacs & Rs 20 lacs respectively. And Increase in expenditure is due to taking up the works of R&M of Road, bridges, Dam and reservoir like repair of toe wall, spillway glacies, protection of hill slope, repair of damaged boulder crate by Rs 196.91 lacs, carrying out of various tests from IIT Roorkee for Rs 15.63 lacs, Repair of service gate for Rs 38.29 lacs, R&M electric works like repair of line from Bhaledh weir to Tissa dam site etc by Rs 26.46 lacs and other misc works for Rs 3.02 lacs and also not taking up the work of premix carpet on Dhargala siul road for Rs 112.15 lac during current period.
2.2 | For Power House and all other works | 57661729 | 72231729 | 25.2681
| Sub-Total (Repair and Maintenance) | 81350802 | 115847851 | 42.4053
|  | 0 | 0
3 | Insurance | 23596861 | 30049774 | 27.3465 | 1). Increase in premium rates on account of deteriorating claim ratio as a result of loss at Dhauliganga & Tanak Pur Power Station due to flood in June 2013 and other factors in the reinsurance market. 2). Increase in sum-insured due to Increase in reinstatement cost of assets on Valuation. 3).Increase in premium rates of CPM Policy on account of deteriorating claim ratio as a result of loss at Dhauliganga Power Station due to flood in June 2013.
4 | Security Expenses | 64395441 | 67665422 | 5.078
|  | 0 | 0
5 | Administrative Expenses | 0 | 0
5.1 | Rent | 5464040 | 5246784 | -3.9761
5.2 | Electricity charges | 26989832 | 26474264 | -1.9102
5.3 | Travelling & Conveyance | 3565898 | 6501541 | 82.3255 | The increase in expenditure is due to revision in the rates (more than double) of TA/DA with effect from 01.04.2014 vide Corporate office Circular no 15/2014 dated 02.04.2014 & as per actual tour & travelling of employees.
5.4 | Telephone, Telex & Postage (Communication) | 3302886 | 3751401 | 13.5795
5.5 | Advertisement | 1530106 | 1778965 | 16.2642
5.6 | Donation | 0 | 0
5.7 | Entertainment | 8250 | 6750 | -18.1818 | Minor expense.
|  | 0 | 0
| Sub-total (Administrative expenses) | 40861012 | 43759705
6 | Employee Cost | 0 | 0
6.1a | Salaries,wages & allow. -Project | 509620549 | 456745566 | -10.3754 | Central Payroll
6.2 | Staff welfare expenses | 36671605 | 35565814 | -3.0154 | Minor
6.3 | Productivity Linked incentive | 17032848 | 21166993 | 24.2716 | PLGI limit was enhanced to 20% from 12.5% of basic pay.
6.4 | VRS-Ex-gratia | 5658109 | 2442898 | -56.8248 | As per actual no employees opted VRS
6.5 | Ex-gratia | 0 | 0
6.6 | Performance related pay (PRP) | 8172154 | 13971814 | 70.9686 | Provision for incremental profit was not taken in F.Y 2013-14. Incremental profit was taken while providing for F.Y 2014-15.
| Sub-total (Employee Cost) | 577155265 | 529893085
7 | Loss of Store | 2574 | 1798 | -30.1476 | Minor Amount
|  | 0 | 0
|  | 0 | 0
9.1 | Allocation of CO Office expenses | 22409834 | 19897079 | -11.2127 | As per advices received
|  | 0 | 0
10 | Others (Specify items) | 10982682 | 12337999 | 12.3405 | Increase is due to R&M of field hostel/ Guest House and due to training expenses.
11 | Total (1 to 10) | 835032934 | 846046220
12 | Revenue /Recoveries | 21162617 | 22138109 | 4.6095
13 | Net Expenses | 813870317 | 823908111
14 | Capital spares consumed not included in A(1) above and not claimed/allowed by commission for capitalisation

## 13-14 vs 12-13
DETAILS OF OPERATION AND MAINTENANCE EXPENSES
Name of the Company : NHPC Ltd
| Name of Power Station: | BAIRASUIL POWER STATION
Reasons for variance
Sl. No. | ITEMS | 2012-13 | 2013-14 | 13-14 vs 12-13 | 13-14 vs 12-13
1
(A) | Breakup of O&M Expenses
1 | Consumption of stores & spares | 15718156 | 14278463 | -9.1594
|  | 0 | 0
2 | Repair & Maintenance | 0 | 0
2.1 | For Dam,Intake,WCS,De-silting chamber | 14831309 | 23689073 | 59.7234 | 1. Increase is due to repair of Thrust Bearing Mirror disc of 60MW Francis trubine for Rs 13.11 lacs and repair of Spherical valve for Rs 14.17 lacs in this year which was not required in last year. 2. Increase is due to carrying out the work of "Providing and lying of premix carpeting on Dargala Siul Road" for Rs 1.20 crore and other special repair work of Bhaledh weir for Rs 0.66 crore which was not done last year.
2.2 | For Power House and all other works | 43238225 | 57661729 | 33.3582
| Sub-Total(Repair &Maintenance) | 58069534 | 81350802 | 40.0921
|  | 0 | 0
3 | Insurance | 18200614 | 23596861 | 29.6487 | 1). Increase in premium rates on account of deteriorating claim ratio as a result of loss at Dhauliganga & Tanak Pur Power Station due to flood in June 2013 and other factors in the reinsurance market. 2). Increase in sum-insured due to Increase in reinstatement cost of assets on Valuation. 3).Increase in premium rates of CPM Policy on account of deteriorating claim ratio as a result of loss at Dhauliganga Power Station due to flood in June 2013 and increase in Sum-insured.
4 | Security Expenses | 62435005 | 64395441 | 3.14
|  | 0 | 0
5 | Administrative Expenses | 0 | 0
5.1 | Rent | 3868574 | 5464040 | 41.2417 | Increase is due to receipt of lease rent advice from ED office Banikhet for Rs 11.18 lacs and also deployment of 2 Nos Bolero this year.
5.2 | Electricity charges | 25974616 | 26989832 | 3.9085
5.3 | Travelling & Conveyance | 3697596 | 3565898 | -3.5617
5.4 | Telephone, Telex & Postage (Communication) | 2121632 | 3302886 | 55.6767 | Increase is due to accountal of liabilties towards Statellite communication expenses(V-SAT) for the year 2013-14 and payment of lease line rent of 4MBPS line to BSNL as compare to last year.
5.5 | Advertisement | 1326748 | 1530106 | 15.3276 | Increase is due to publishing of more press tender as compared to last year.
5.6 | Donation | 0 | 0
5.7 | Entertainment | 9000 | 8250 | -8.3333
|  | 0 | 0
| Sub-total (Administrative expenses) | 36998166 | 40861012
6 | Employee Cost | 0 | 0
6.1a | Salaries,wages & allow. -Project | 507537042 | 509620549 | 0.41051
6.2 | Staff welfare expenses | 21835346 | 36671605 | 67.9461 | Due to increase in retired employees medical benefit actuarial valuation provision as compare to last year.
6.3 | Productivity Linked incentive | 34935418 | 17032848 | -51.2448 | 1). In F.Y 2012-13, this expenditure was more than FY 2013-14 due to PLGI from 2007-2010 on revised pay was paid in 2012-13.
6.4 | VRS-Ex-gratia | 3348399 | 5658109 | 68.9795 | On the basis of Actual no. of Employees opted for VRS
6.5 | Ex-gratia | 0 | 0
6.6 | Performance related pay (PRP) | 16128526 | 8172154 | -49.3311 | In FY 2012-13, this expenditure was more than FY 2013-14 due to payment of PRP for F.Y 2010-11 & F.Y 2011-12 during F.Y 2012-13.
| Sub-total (Employee Cost) | 583784731 | 577155265
7 | Loss of Store | 83365 | 2574 | -96.9124 | As per actual
|  | 0 | 0
|  | 0 | 0
9.1 | Allocation of CO Office expenses | 25307956 | 22409834 | -11.4514 | As per advices received
|  | 0 | 0
10 | Others (Specify items) | 8271545 | 10982682 | 32.7767 | Increase is due to R&M of field hostel/ Guest House and due to training expenses.
11 | Total (1 to 10) | 808869072 | 835032934
12 | Revenue /Recoveries | 86685362 | 21162617 | -75.5869 | Due to decrease in Provision/Liability not required written back and decrease in other income.
13 | Net Expenses | 722183710 | 813870317
14 | Capital spares consumed not included in A(1) above and not claimed/allowed by commission for capitalisation