## Annexure-III 1 to 3
Annexure-III
SH 1/3
Pro-forma for furnishing Actual annual performance/operational data for the Hydro Electric generating stations for the 5-year period from 2012-13 to 2016-17
| Particulars |  | Units | 2012-13 | 2013-14 | 2014-15 | 2015-16 | 2016-17
1 | Name of Company |  |  | NHPC LTD.
2 | Name of Station |  |  | Parbati-III Power Station
3 | Installed Capacity and Configuration |  | (MW) | 520
4 | Station Location |  | Under ground or Surface | Under Ground
5 | Type of Excitation System |  |  | Static
6 | Live Storage Capacity |  | (Million Cubic) | 0.98
7 | Rated Head |  | Metres | 326 M | 326 M | 326 M | 326 M | 326 M
8 | Head at Full Reservoir Level (FRL) |  | Metres | 334.3 M | 334.3 M | 334.3 M | 334.3 M | 334.3 M
9 | Head at Minimum Draw down Level (MDDL) |  | Metres | 315.3 M | 315.3 M | 315.3 M | 315.3 M | 315.3 M
10 | MW Capability at FRL |  | MW | - | 390 MW | 520 MW | 520 MW | 520 MW
11 | MW Capability at MDDL |  | MW | - | 390 MW | 490 MW | 490 MW | 490 MW
12 | Cost of spares :
12.1 | Cost of spares capitalized in books of accounts |  | (Rs. Lakhs) | -
12.2 | Cost of spares included in the capital cost for the purpose of tariff |  | (Rs. Lakhs) | - | Cost of the spares is included in the cost of major plant equipments supplied by M/s BHEL under major works contract (Lot-IV E&M Works)
Period
13 | Generation :
13.1 | Actual Gross Generation at Generator Terminals |  | (MU) | - | 4.81 | 660.7631 | 643.0002 | 682.4881
13.2 | Actual Net Generation Ex-bus including free power |  | (MU) | - | 4.78 | 656.0935 | 640.9291 | 680.5849
13.3 | Scheduled generation Ex-bus including free power |  | (MU) | - | 2.7005 | 648.1137 | 631.546 | 666.6849
14 | Actual Auxiliary Energy Consumption excluding colony consumption |  | (MU) | - | 0.03 | 3.6113 | 4.5749 | 4.9041
15 | Actual Energy supplied to Colony from the station |  | (MU) | - | NIL | NIL | NIL | NIL
16 | Average Declared Capacity (DC) during the year |  | (MW) | - | 14.45 | 180 | 216.55 | 274.17
Annexure-III
SH 2/3
| Period |  | Units | 2012-13 | 2013-14 | 2014-15 | 2015-16 | 2016-17
17 | Weighted Average duration of outages ( Unit-wise details)
17.1 | Scheduled outages |  | (Days) | 0 | 0 | 478.057 | 589.7402 | 418.4049
17.2 | Forced outages |  | (Days) | 0 | 11.8188 | 256.2492 | 114.2174 | 41.2438
18 | Cost of spares actually consumed |  | (Rs. Lakhs) | - | - | 91.03 | 200.47 | 296.03
19 | Average stock of spares |  | (Rs. Lakhs) | - | - | 80 | 170 | 225
Month wise Design Energy
Month |  | Period | Design Energy as approved by CEA (MU) |  | Month | Period | Design Energy as approved by CEA (MU)
April |  | 1-10 | 10.91 |  | October | 1-10 | 13.67
|  | 11-20 | 18.51 | 18.51 |  | 11-20 | 12.07 | 12.07
|  | 21-30 | 15.34 | 15.34 |  | 21-31 | 11.63 | 11.63
May |  | 1-10 | 16.92 | 16.92 | November | 1-10 | 9.08 | 9.08
|  | 11-20 | 24.09 | 24.09 |  | 11-20 | 8.23 | 8.23
|  | 21-31 | 25.48 | 25.48 |  | 21-30 | 7.6 | 7.6
June |  | 1-10 | 40.58 | 40.58 | December | 1-10 | 6.8 | 6.8
|  | 11-20 | 36.5 | 36.5 |  | 11-20 | 6.44 | 6.44
|  | 21-30 | 37.63 | 37.63 |  | 21-31 | 6.5 | 6.5
July |  | 1-10 | 43.47 | 43.47 | January | 1-10 | 5.73 | 5.73
|  | 11-20 | 44.88 | 44.88 |  | 11-20 | 5.68 | 5.68
|  | 21-31 | 58.74 | 58.74 |  | 21-31 | 5.77 | 5.77
August |  | 1-10 | 39.58 | 39.58 | February | 1-10 | 4.82 | 4.82
|  | 11-20 | 33.98 | 33.98 |  | 11-20 | 4.38 | 4.38
|  | 21-31 | 43.25 | 43.25 |  | 21-28 | 4.51 | 4.51
September |  | 1-10 | 31.56 | 31.56 | March | 1-10 | 5.55 | 5.55
|  | 11-20 | 22.83 | 22.83 |  | 11-20 | 8.66 | 8.66
|  | 21-30 | 19.78 | 19.78 |  | 21-31 | 10.25 | 10.25
[5 empty] | Total |  | 701.4
Storage Hydro plants shall also furnish actual monthly average peaking generation in MW achieved during the period 2012-13 to 2016-17 against the monthly average peaking capability approved by CEAas per following format:
Month |  | Expected Avg. of daily 3-hour peaking capacity as approved by CEA |  |  | Actual monthly average of daily 3-hour peaking (MW) for the period 2012-13 to 2016-17
April |  | 400.11 |  |  |  | 122.9146
May |  | 437.19 |  |  |  | 131.0241
June |  | 507.27 |  |  |  | 155.7646
July |  | 513.76 |  |  |  | 154.7762
August |  | 504.73 |  |  |  | 165.4869
September |  | 451.05 |  |  |  | 190.4146
October |  | 385.12 |  |  |  | 133.8353
November |  | 276.37 |  |  |  | 73.5772
December |  | 212.45 |  |  |  | 43.7543
January |  | 184.79 |  |  |  | 27.8778
February |  | 164.62 |  |  |  | 38.6837
March |  | 6261.04 |  |  |  | 69.8279
Annexure III
SH 3/3
1 | List of beneficiaries/customers along with allocation by GoI including (allocation of unallocated share) / capacity as contracted should also be furnished separately for each generating station.
2 | Declared Capacity should be as per Regulation 31(3) of CERC Tariff Regulations for the period 2014-19 including month wise information may be furnished.
3 | Any relevant point or a specific fact having bearing on performance or operating parameters may also be highlighted or brought to the notice of the Commission.
Design Energy
In clause 19 to 23 of CERC Order dated 24/06/2014 in Petition No 228/GT/2013, it has been delibrated that the completion of upstream Parbati-II HEP has been delayed due to various reasons and the said project could not be made operational prior to the commissioning of Parbati-III. The tail race water of Parbati-II HEP would not be available for generation at this project and therefore, this generating station would operate as ROR scheme till the commissioning of upstream Parbati-II HEP, based on the fact that the live storage capacity of this project is only 1.28 MCM which is not sufficient to provide minimum three hours peaking with four units.
The post-sedimentation live storage capacity is only 0.87 MCM which is just sufficient to meet 1.36 hours of peaking. The annual design energy of this project, on stand-alone basis, till the commissioning of upstream Parbati-II HEP, with downstream discharge as 1.15 cumecs and updated discharge series (1973-74 to 2010-11) approved by CEA, in a 90% dependable year would be 701.40 Million Units. It has stated that the design energy of this project would be reviewed by CEA on the commissioning of upstream Parbati-II HEP. Considering the above, we allow the design energy of 701.40 Million Units as approved by CEA till the commissioning of the upstream Parbati-II HEP.
Normative annual plant availability factor (NAPAF)
(a) It is mentioned in the DPR of the project, as cleared by CEA that Parbati-III HEP will operate as ROR scheme till commissioning of upstream Parbati-II HEP. This is based on the fact that the live storage capacity of Parbati-III HEP is only 1.28 MCM which is not sufficient to provide minimum three hours peaking with four units. (b) Similarly, the post-sedimentation live storage capacity is only 0.87 MCM which is just sufficient to meet 1.36 hours of peaking. The NAPAF for Parbati-III HEP which has been claimed at 31% is actually based on the operation of the power station as ROR scheme. The same will be reviewed after commissioning of Parbati-II HEP.
Peaking operation of the plant
To operate the project as 'Run of River' project till the upstream Parbati-II HEP is commissioned. However, the live storage capacity of 1.28 MCM is available which can be utilized to provide peaking power. On perusal of the design energy data and corresponding inflows, it is observed that the generating station can provide 3 hours of daily peaking depending on the inflows. However, due to reduced inflows on account of the non-commissioning of upstream Parbati-II HEP, this generating station would be able to provide maximum available peaking support for three hours in two slots of 1.5 hours each (morning & evening peak). In view of the fact that the generating station has been designed to operate in peaking mode and for that purpose a dam has been constructed whose cost has been embedded in the cost of the project, we find it prudent that the generating station should be operated to provide peaking support to the grid. Accordingly, it was direct to provide 1.5 hours of peaking in two slots of morning & evening

## Annexure-IV
Annexure –IV
PLANT AVAILABILITY/SCHEDULED PLANT LOAD FACTOR ACHIEVED Generating company: NHPC LTD. Name of Generating station: Parbati-III Power Station Installed Capacity (MW) : 520 MW Normative Annual Plant Availability Factor (%) approved by Commission : 68%
Plant Availability Factor Achieved (%)
Month | 2012-13 | 2013-14 | 2014-15 | 2015-16 | 2016-17 | Reasons for shortfall in PAF achieved vis-a-vis NAPAF
April |  |  | 54.6256 | 55.9802 | 51.7319 | # | 122.9146
May |  |  | 66.7055 | 62.3067 | 52.5118 |  | 131.0241
June |  |  | 52.6836 | 70.7096 | 65.7895 |  | 155.7646
July |  |  | 50.4566 | 58.8378 | 76.7952 |  | 154.7762
August |  |  | 43.8798 | 57.8174 | 87.2015 |  | 165.4869
September |  |  | 23.6695 | 72.0451 | 94.8184 |  | 190.4146
October |  |  | 42.5299 | 51.5722 | 65.7099 |  | 133.8353
November |  |  | 23.0106 | 25.6562 | 38.8207 |  | 73.5772
December |  |  | 0 | 11.2757 | 27.0669 |  | 43.7543
January |  |  | 0 | 0 | 24.4298 |  | 27.8778
February |  |  | 24.3107 | 8.1437 | 25.7555 |  | 38.6837
March |  | 44.4652 | 38.3633 | 31.4663 | 29.7251 |  | 69.8279
Annual | 0 | 44.4652 | 33.8819 | 42.1843 | 53.4866
# Major Outages impacting PAF are as Under:
DURING 2014-15 : 1. OUTAGE OF U#1 W.E.F 26/03/2014 TO 20/04/2014 DUE TO ROTOR EARTH FAULT. 2. OUTAGE OF U#1 W.E.F 23/08/2014 TO 11/08/2014 FOR INSPECTION OF UNDERWATER PARTS. 3. OUTAGE OF U#1 W.E.F 28/03/2015 TO 31/03/2015 FOR REPAIR OF STATOR WINDING. UNIT RESTORED ON 26/07/2016. 4. OUTAGE OF U#3 W.E.F 13/05/2014 TO 18/11/2014 DUE TO R-PHASE TRANSFORMER SHIFTED TO UNIT#4 5. OUTAGE OF U#4 W.E.F 07/06/2014 TO 09/10/2014 FOR REPAIR OF UNDERWATER PARTS. 6. COMPLETE SHUTDOWN OF POWER STATION W.E.F 19/11/2014 TO 02/02/2015 DUE TO RECTIFICATION OF WATER LEAKAGE FROM WATER CONDUCTOR SYSTEM & PRESSURE SHAFTS.
DURING 2015-16: 1. OUTAGE OF U#1 W.E.F 28/03/2015 FOR REPAIR OF STATOR WINDING. 2. U#2 W.E.F 26-MAR-2015 TO 07-APR-2015 DUE TO EXCESSIVE LEAKAGE FROM EXPANSION JOINT AT DOWNSTREAM OF MIV. 3. U#2 W.E.F 18-MAY-2015 TO 05-JUN-2015 FOR RECTIFICATION OF HIGH LGB PAD TEMPERATURE. 4. COMPLETE SHUTDWON OF POWER STTAION W.E.F 18-JUL-2015 TO 22-JUL-2015 DUE TO HIGH SILT IN HRT AND CHOKING OF COOLING WATER SYSTEM DUE TO FLASH FLOOD & CLOUD BURST. 5. U#2 W.E.F 27-AUG-2015 TO 31-AUG-2015 DUE TO STATOR EARTH FAULT. 6. U#3 W.E.F 14-AUG-2015 TO 28-AUG-2015 DUE TO SHEAR PIN BROKEN & HIGH LGB VIBRATIONS. 7. U#4 W.E.F 22-AUG-2015 TO 27-AUG-2015 DUE TO INSPECTION OF UNDERWATER PARTS(ABNORMAL SOUND). 8. U#3 W.E.F 25-SEP-2015 TO 30-SEP-2015 FOR DISMANTLING OF UAT. 9. COMPLETE SHUTDOWN OF POWER STATION W.E.F 15-DEC-2015 TO 04-FEB-2016 FOR REPAIR OF PRESSURE SHAFT .
DURING 2016-17: 1. U#1 RESTORED ON 26/07/2016, WHICH WAS UNDER OUTAGE FROM 28/03/2015 FOR REPAIR OF STATOR WINDING. 2. U#1 W.E.F 24-AUG-2016 TO 02-JUN-2016 DUE TO HIGH UGB PAD TEMPERATURE. 3. U#3 W.E.F 18-JUL-2016 TO 20-JUL-2016 , FROM 19-AUG-2016 TO 20-AUG-2016 & FROM 21-SEP-2016 TO 24-SEP-2016 DUE TO SHEAR PIN FAILURE. 4. U#4 W.E.F 19-AUG-2016 TO 21-AUG-2016 & FROM 30-AUG-2016 TO 31-AUG-2016 DUE TO SHEAR PIN FAILURE.
Plant Load Factor Achieved (%)
Month | 2012-13 | 2013-14 | 2014-15 | 2015-16 | 2016-17 | Reasons for shortfall in PLF achieved vis-a-vis Target PLF
April
May
June
July | NA
August
September
October
November
December
January
February
March
Annual

## Annexure-XIX (PARBATI-III)
Annexure-XIX
Name of the Utility |  | NHPC LTD.
Name of the Generating Station |  | Parbati-III Power Station
Station/ Stage/ Unit |  | 4x130 MW
Fuel Type (Coal/ Lignite/ Gas/ Liquid Fuel/ Nuclear/ Hydro | [7 empty] | Hydro
Capacity of Plant (MW) |  | 520 MW
COD |  | 2014-06-06
|  | 2004-05 | 2005-06 | 2006-07 | 2007-08 | 2008-09 | 2009-10 | 2010-11 | 2011-12 | 2012-13 | 2013-14 | 2014-15 | 2015-16 | 2016-17
1 | Plant Availability Factor (PAF) (%) | 2014-06-06 2004-05: Not Commissioned; 2014-06-06 2013-14: 44.4652; 2014-06-06 2014-15: 33.8819; 2014-06-06 2015-16: 42.1843; 2014-06-06 2016-17: 53.4866
2 | Plant Load Factors (PLF) (%)
3 | Scheduled Energy (MU) | 2014-06-06 2004-05: Not Commissioned; 2014-06-06 2013-14: 2.7005; 2014-06-06 2014-15: 648.1139; 2014-06-06 2015-16: 631.1027; 2014-06-06 2016-17: 666.6849
4 | Scheduled Generation (MU)
5 | Actual Generation (MU) | 2014-06-06 2004-05: Not Commissioned; 2014-06-06 2013-14: 4.78; 2014-06-06 2014-15: 660.7631; 2014-06-06 2015-16: 643.0002; 2014-06-06 2016-17: 682.4881
6 | Quantum of coal consumption (MT)
7 | Value of coal (Rs. Lakh)
8 | Specific Coal Consumption (kg/kwh)
9 | Gross Calorific Value of Coal (Kcal/ Kg)
10 | Heat Contribution of Coal (Kcal/ kwh)
11 | Cost Of Specific Coal Consumption (Rs./Kwh) – Finally admitted by CERC
12 | Quantum of Oil Consumption (Lit.)
13 | Value of Oil (Rs. lakh)
14 | Gross calorific value of oil (kcal/lit)
15 | Specific Oil Consumption (ml/ kwh)
16 | Cost Of Specific Oil Consumption (Rs./Kwh) – Finally admitted by CERC
17 | Heat Contribution of Oil (Kcal/ kwh)
18 | Station Heat Rate (kcal/kwh)
19 | Auxiliary Energy Consumption (%) | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ---- | 0.6 | 0.54857 | 0.71064 | 0.71565
20 | Debt at the end of the year (Rs. Crore) | 2014-06-06 2013-14: 1123.8014
21 | Equity (Rs. Crore) | 2014-06-06 2013-14: 482.1912
22 | Working Capital (Rs. Crore) – finally admitted by CERC
23 | Capital cost (Rs. Crore) – finally admitted by CERC | 2014-06-06 2013-14: 1607.304
24 | Capacity Charges/ Annual Fixed Cost (AFC)
(a) Return on equity – pre tax (admitted by CERC)
| Absolute value | 2014-06-06 2013-14: 1.6517
Rate (%)
(b) interest on Loan
| Absolute value | 2014-06-06 2013-14: 1.792
Rate (%) – Weighted Average Rate
(c) Depreciation (finally allowed by CERC)
| Absolute value | 2014-06-06 2013-14: 1.3114
Rate (%)
(d) Interest on working Capital
| Absolute value | 2014-06-06 2013-14: 0.1354
Rate (%)
(e) Operation and maintenance cost (finally admitted by CERC)
| Absolute value | 2014-06-06 2013-14: 0.5265
Rate (%)
(f) Compensation Allowances | bar: 2014-06-06 2004-05
25 | AFC (Rs. Crores) | 2014-06-06 2013-14: 5.417
26 | Energy Charge (Rs./Kwh)
27 | Total tariff (Rs. Kwh)
28 | Revenue realisation before tax (Rs. Crore) | 2014-06-06 2013-14: 4.9523; 2014-06-06 2014-15: 278.8365; 2014-06-06 2015-16: 367.2054; 2014-06-06 2016-17: 386.5418
29 | Revenue realisation after tax (Rs. Crore) #
30 | Profit/ loss before tax(Rs. Crore) | 2014-06-06 2013-14: -1.3242; 2014-06-06 2014-15: -51.5181; 2014-06-06 2015-16: 19.0693; 2014-06-06 2016-17: 65.6415
31 | DSM Generation (MU) | 2014-06-06 2004-05: Not Commissioned; 2014-06-06 2013-14: 1.329; 2014-06-06 2014-15: 11.3045; 2014-06-06 2015-16: 9.8288; 2014-06-06 2016-17: 13.9259
32 | DSM Rate (Ps/Kwh)
33 | Revenue from DSM (Rs. Crore) | 2014-06-06 2013-14: -0.41071; 2014-06-06 2014-15: 1.2927; 2014-06-06 2015-16: 1.6305; 2014-06-06 2016-17: 2.7539
1. The data at Sl No. 20 to 27 has been filled based on CERC ADHOC tariff order dated 28.03.2016. The final tariff order yet to be issued by CERC.
2. The capital cost sl no. 23 & equity at sl no. 21 has been considered as closing equity & capital cost respectively as on 31st March of respective year.
3. The billing for the period 2014-19 is being carried out based on allowed AFC for 2013-14 converted pro-rata for 365 days.
4. # NHPC calculate Corporate Tax as a whole after considering all the admissible deductions, exemptions etc. as per Income Tax Act. Therefore unitwise calculation has not been made.
Note: Generating Companies are required to submit data for all generating stations.
This is a general format. Plants of different fuel users have to fill the cells as applicable to them. Tariff for the Hydro may be understood as composite tariff.
The data provided for the corresponding years need to mention as Actual or provisional.
Data for each Unit and Stage is required to be submitted in additional sheets as per the format.

## 2012-13 vs 2013-14
DETAILS OF OPERATION AND MAINTENANCE EXPENSES
Name of the Company : NHPC Ltd
Name of Power Station: PARBATI III POWER STATION
Sl. No. | ITEMS | 2012-13 | 2013-14
1
(A) | Breakup of O&M Expenses
1 | Consumption of stores & spares |  | 0
0
2 | Repair & Maintenance |  | 0
2.1 | For Dam,Intake,WCS,De-silting chamber |  | 84412
2.2 | For Power House and all other works |  | 241521
| Sub-Total (Repair and Maintenance) | 0 | 325933
0
3 | Insurance |  | 358686
4 | Security Expenses |  | 330712
0
5 | Administrative Expenses |  | 0
5.1 | Rent |  | 541950
5.2 | Electricity charges |  | 645279
5.3 | Travelling & Conveyance |  | 1926784
5.4 | Telephone, Telex & Postage (Communication) |  | 69955
5.5 | Advertisement |  | 1242401
5.6 | Donation |  | 0
5.7 | Entertainment |  | 54800
0
| Sub-total (Administrative expenses) | 0 | 4481169
6 | Employee Cost |  | 0
6.1a | Salaries,wages & allow. -Project |  | -208207228
6.2 | Staff welfare expenses |  | 15835543
6.3 | Productivity Linked incentive |  | 5238836
6.4 | VRS-Ex-gratia |  | 0
6.5 | Ex-gratia |  | 0
6.6 | Performance related pay (PRP) |  | 10508292
| Sub-total (Employee Cost) | 0 | -176624557
7 | Loss of Store |  | 0
0
0
9.1 | Allocation of CO Office expenses |  | 191241237
0
10 | Others (Specify items) |  | 1859021
11 | Total (1 to 10) | 0 | 21972201
12 | Revenue /Recoveries |  | 19384502
13 | Net Expenses | 0 | 2587699
14 | Capital spares consumed not included in A(1) above and not claimed/allowed by commission for capitalisation

## 2013-14 vs 2014-15
DETAILS OF OPERATION AND MAINTENANCE EXPENSES
Name of the Company : NHPC Ltd
| Name of Power Station: | PARBATI III POWER STATION
Sl. No. | ITEMS | 2013-14 | 2014-15 |  | Reason of variances 2013-14 & 2014-15
1
(A) | Breakup of O&M Expenses
1 | Consumption of stores & spares | 0 | 0
|  | 0 | 0
2 | Repair & Maintenance | 0 | 0
2.1 | For Dam,Intake,WCS,De-silting chamber | 84412 | 6881627 | 98.7734 | Two units of Parbati III was commissioned on 24th March 2014 & IIIrd unit on 30th March 2014 therfore expenditure is lower side in 2013-14. However, expenditure increased due to deployment of outsourced staff for operation of Dams, purchase of necessary consumables .
2.2 | For Power House and all other works | 241521 | 31048966 | 99.2221 | Two units of Parbati III was commissioned on 24th March 2014 & IIIrd unit on 30th March 2014 therfore expenditure is lower side in 2013-14.. However expenditure increased due to deployment of outsourced staff for PH, purchase of essential consumables for PH and expenditure on annual maintt. of machines.
| Sub-Total (Repair and Maintenance) | 325933 | 37930593
|  | 0 | 0
3 | Insurance | 358686 | 41571323 | 99.1372 | Mega insurance policy has been taken in 2014-15 and therefore expenditure increased
4 | Security Expenses | 330712 | 19012730 | 98.2606 | Exp before transfer to EDC is 1.66cr in 2013-14 and it increased in 2014-15 due to increase in Security perosonnel for watch and ward of assets handed over to project by contractor after commsioning.
|  | 0 | 0
5 | Administrative Expenses | 0 | 0
5.1 | Rent | 541950 | 23506227 | 97.6944 | Exp before transfer to EDC 2.48 Crore in 2013-14 and wtinin the range of 10%
5.2 | Electricity charges | 645279 | 24373581 | 97.3525 | Exp before transfer to EDC 2.85 Crore in 2013-14 and wtinin the range of 10%
5.3 | Travelling & Conveyance | 1926784 | 6043023 | 68.1156 | Exp before transfer to EDC 52 lacs in 2013-14 and increased due to hike in DArates , Hotel entitledment and conveyence charges
5.4 | Telephone, Telex & Postage (Communication) | 69955 | 4484428 | 98.44 | Exp before transfer to EDC 43 lacs in 2013-14 and wtinin the range of 10%
5.5 | Advertisement | 1242401 | 1425366 | 12.8364 | Variance within 10%
5.6 | Donation | 0 | 0
5.7 | Entertainment | 54800 | 43800 | -25.1142 | Vary due decrease/ increase in nos of Chief Engineers and above.
|  | 0 | 0
| Sub-total (Administrative expenses) | 4481169 | 59876425
6 | Employee Cost | 0 | 0
6.1a | Salaries,wages & allow. -Project | -208207228 | 287255508 | 172.4815 | Exp before transfer to EDC 28Crore in 2013-14 and wtinin the range of 10%
6.2 | Staff welfare expenses | 15835543 | 18976694 | 16.5527 | Expenditure increased more than 10% due to increase in Medical reimbursement and cost of medicine ( for detailed see below)
6.3 | Productivity Linked incentive | 5238836 | 6471189 | 19.0437 | Expenditure depend rate of PLI fixed by CO & nos of empolyees in the project
6.4 | VRS-Ex-gratia | 0 | 3492616 | 100 | 01 case of VRS in 2014-15
6.5 | Ex-gratia | 0 | 0
6.6 | Performance related pay (PRP) | 10508292 | 17492966 | 39.9285 | Expenditure depend upon the rating of NHPC, KPA and nos of empolyees in the project
| Sub-total (Employee Cost) | -176624557 | 333688973
7 | Loss of Store | 0 | 0
|  | 0 | 0
|  | 0 | 0
9.1 | Allocation of CO Office expenses | 191241237 | 161716394 |  | Allocation given by CO
|  | 0 | 0
10 | Others (Specify items) | 1859021 | 20075532 | 90.7399 | See below
11 | Total (1 to 10) | 21972201 | 673871970
12 | Revenue /Recoveries | 19384502 | 5145537
13 | Net Expenses | 2587699 | 668726433
14 | Capital spares consumed not included in A(1) above and not claimed/allowed by commission for capitalisation

## 2014-15 vs 2015-16
DETAILS OF OPERATION AND MAINTENANCE EXPENSES
Name of the Company : NHPC Ltd
| Name of Power Station: | PARBATI III POWER STATION
Sl. No. | ITEMS | 2014-15 | 2015-16 |  | Reason of variances 2014-15 & 2015-16
1
(A) | Breakup of O&M Expenses
1 | Consumption of stores & spares | 0 | 0
|  | 0 | 0
2 | Repair & Maintenance | 0 | 0
2.1 | For Dam,Intake,WCS,De-silting chamber | 6881627 | 10069946 | 46.3309 | Exp increased due to 1) Repair of diversion tunnel for Rs.5.5lacs . 2) Repair of HRT for Rs. 4lacs. 3) Repair of civil HM work for Rs.10lacs.4) Hiring of raft fro dam. 5) General Increase in minimum wage rate of workers deployed for operation and maintt. of Dam. These all expenditure are essential for soomth running of water conductor system.
2.2 | For Power House and all other works | 31048966 | 42692761 | 37.5014 | Expenditure increased due to 1) Purchase of additional various consumables for PH viz. prime servo oil of Rs.44lacs, purchase of pressure switch, rotor lifting bolts , coupling capcitors and others spares of worth Rs.26lacs. 2) expenditure of annual maintt. Of Rs.45lacs 3) expenditure on other works viz. development of area around D-type qtrs for Rs4lacs., repair of store shed at sallah for Rs.4.5lacs, repair and manitt of store nead admn building for Rs.5.5lacs and purchase of misc items for office of Rs.3lacs.4) expenditure also increased due to hike in minimum wage paid to worker deployed for operation maintt. amd upkeeping of power house.These all expenditure are essential for the smooth running of Power house.
| Sub-Total (Repair and Maintenance) | 37930593 | 52762707
|  | 0 | 0
3 | Insurance | 41571323 | 58740746 | 41.3011 | In case of Mega Insurance Police 1. Increase in premium rates on account of deteriorating claim ratio as a result of loss due Fire incident at Uri-II Power Station and submergence of Chutak power Station in November 2014 and June 2015 respectively and other claims during policy period 2014-15 2. Increase in sum-insured due to increase in reinstatement cost of assets on Valuation. 3. Increase in the rate of Service Tax and WCT from 12.36% to 14% and 10.5% to 12.6% respectively. In case of CPM policy, Increase in Sum insured due to valuation of Assets, additional Construction equipment purchased and increase in premium rates & Service Tax/WCT rates as above.
4 | Security Expenses | 19012730 | 68794349 | 261.8331 | Expenditure increased due to deployment of CISF for the watch and ward of Project after commisioning as per the guidelines of Government.
|  | 0 | 0
5 | Administrative Expenses | 0 | 0
5.1 | Rent | 23506227 | 22254639 | -5.3245
5.2 | Electricity charges | 24373581 | 28198883 | 15.6945 | Electrcity charges increased due to deployemnt of CISFi.e. Electricity used by CISF for office and security posts etc.
5.3 | Travelling & Conveyance | 6043023 | 6014593 | -0.47046
5.4 | Telephone, Telex & Postage (Communication) | 4484428 | 4974104 | 10.9195 | within 10% variance
5.5 | Advertisement | 1425366 | 3206537 | 124.9624 | Expenditure increased due to huge increase in tendering. Increase in tendering leads to higher expenditure under the head advertisement tenders. These tenders were floated to complete the work of Add cap and to procure the intitial spares
5.6 | Donation | 0 | 0
5.7 | Entertainment | 43800 | 32754 | -25.2192 | Vary due decrease/ increase in nos of Chief Engineers and above.
|  | 0 | 0
| Sub-total (Administrative expenses) | 59876425 | 64681510
6 | Employee Cost | 0 | 0
6.1a | Salaries,wages & allow. -Project | 287255508 | 287626705 | 0.12922 | within 10% variance
6.2 | Staff welfare expenses | 18976694 | 16069593 | -15.3193 | Decrease due to Reduction in RETIRED EMPLOYEES MEDICAL BENEFIT ACTUARIAL VALUATION PROVISION and medical expenses in comparison to 2014-15
6.3 | Productivity Linked incentive | 6471189 | 5921430 | -8.4955
6.4 | VRS-Ex-gratia | 3492616 | 11701524 | 235.0361 | No of employees opted for VRS in 2015-16 is more as compared to 2014-15.
6.5 | Ex-gratia | 0 | 0
6.6 | Performance related pay (PRP) | 17492966 | 17888805 | 2.2628
| Sub-total (Employee Cost) | 333688973 | 339208057 | 1.654
7 | Loss of Store | 0 | 0
|  | 0 | 0
|  | 0 | 0
9.1 | Allocation of CO Office expenses | 161716394 | 133298170 |  | Allocation given by CO
|  | 0 | 0
10 | Others (Specify items) | 20075532 | 28434424 | 41.6372 | This expenditure of Rs 10,96,926/-was incurred for repair of larji behali bye pass road in 2015-16 (Expenditure on Assets not belonging to Corporation). This road is vital to the project and alternate to access the project in case blockade of main road . This expenditure of Rs 75,79,107/-pertains to foregn exchange payments and reinstatement of foreign exhange liabilities in books on each balance sheet date. Amount may vary depending upon the foregn exhange rate at the time of payments or on balancesheet date
11 | Total (1 to 10) | 673871970 | 745919963
12 | Revenue /Recoveries | 5145537 | 11849373 | 130.2845 | Rs 5723089/- was realised on account of ERV gain. Amount may vary depending upon the foregn exhange rate at the time of payments or on balancesheet date. Increase in Other Income on account of other miscellaneous incomes.
13 | Net Expenses | 668726433 | 734070590
14 | Capital spares consumed not included in A(1) above and not claimed/allowed by commission for capitalisation

## 2015-16 vs 2016-17
DETAILS OF OPERATION AND MAINTENANCE EXPENSES
Name of the Company : NHPC Ltd
| Name of Power Station: | PARBATI III POWER STATION
Sl. No. | ITEMS | 2015-16 | 2016-17 | Variance (%) | Reason of variances 2015-16 & 2016-17
1
(A) | Breakup of O&M Expenses
1 | Consumption of stores & spares | 0 | 11976672 | 100 | Store and spares of 1.19crore have been purchased for the smooth functioning of PH which are detailed below: HIGH HOLE SAW CUTTER BIT COMPLETE 3/4 INCH,TEFLON TAPE, HACK SAW FRAME, DIGITAL CARD, INTERRUPTGENERATORMODUL, WELDING ELECTRODE SS , FILTER ELEMENT T LINE , CYLINDER HP 3 T LINE, CAP ASSEMBLY CRANKPIN, RUBBER CORD DIA, COTTON CUTTING BANYAN CLOTH, DIGITAL CARDs, MDL 69203YB2BA UNS 2662,PULSE COUPLING STAGE,UN-0096A, AC-DC SUPPLY MODULE UNC4664AV1 69203PZ1AA,POTENTIAL SEPERATING UNIT,PANEL METER WITH CONTROL UNIT RIA45,PAINT IN PH,LOG BOOK FOR GSU TRANSFORMER PANELREFILLING CYLINDER OF OXYGEN CYLINDER,INSERT SOCKET 105MM AF M - 105MM AF F, SOCKET LENGTH,
|  | 0 | 0
2 | Repair & Maintenance | 0 | 0
2.1 | For Dam,Intake,WCS,De-silting chamber | 10069946 | 7328616 | -27.2229 | Exp in 2015-16 was increased due to 1) Repair of diversion tunnel for Rs.5.5lacs . 2) Repair of HRT for Rs. 4lacs. 3) Repair of civil HM work for Rs.10lacs.4) Hiring of raft fro dam. 5) General Increase in minimum wage rate of workers deployed for operation and maintt. of Dam which was not required in the year 2016-17.
2.2 | For Power House and all other works | 42692761 | 51398244 | 20.391 | Expenditure increased due to 1) Additional maintt. Exp of machines of Rs.33lacs. 2) Additional AMC of electrical installation equipments viz AC etc.of Rs.11lacs.3) upgrading of local area network of Rs.3lacs. General increase in the maintt. Of electrical installation inclusive of AMC of DG sets, UPS etc. .4) expenditure also increased due to hike in minimum wage paid to worker deployed for operation maintt. amd upkeeping of power house.These all expenditure are essential for the smooth running of Power house.
| Sub-Total (Repair and Maintenance) | 52762707 | 58726860
|  | 0 | 0
3 | Insurance | 58740746 | 60926627 | 3.7212
4 | Security Expenses | 68794349 | 96119912 | 39.7207 | Mainly expenditure increased due to revision of payscale wef Jan-2016 in r/o CISF
|  | 0 | 0
5 | Administrative Expenses | 0 | 0
5.1 | Rent | 22254639 | 20824831 | -6.4248 | within 10% variance
5.2 | Electricity charges | 28198883 | 28753461 | 1.9667 | within 10% variance
5.3 | Travelling & Conveyance | 6014593 | 6185027 | 2.8337 | within 10% variance
5.4 | Telephone, Telex & Postage (Communication) | 4974104 | 4774203 | -4.0188 | within 10% variance
5.5 | Advertisement | 3206537 | 3743127 | 16.7343 | Mainly expenditure increase under Misc public relation incurred for maintaining good rapport with State officials.
5.6 | Donation | 0 | 0
5.7 | Entertainment | 32754 | 34854 | 6.4114 | Vary due decrease/ increase in nos of Chief Engineers and above.
|  | 0 | 0
| Sub-total (Administrative expenses) | 64681510 | 64315503
6 | Employee Cost | 0 | 0
6.1a | Salaries,wages & allow. -Project | 287626705 | 323150140 | 12.3505 | Exp increased due to provsioning of 3months exp of salary on account of wage revision from Jan-17
6.2 | Staff welfare expenses | 16069593 | 10862164 | -32.4055 | Project commissioning awad is also included in 2015-16 exp. Therefore there is large variance between 2015-16 and 2016-17( for detail see below)
6.3 | Productivity Linked incentive | 5921430 | 12884016 | 117.5828 | Increase due to payment of arear of PLGI at revised rate from F.Y 2010-11 to F.Y 2013-14 and provision of PLGI for Q4 of FY 2016-17 made on revised pay
6.4 | VRS-Ex-gratia | 11701524 | 0 | -100 | NO VRS case in 2016-17
6.5 | Ex-gratia | 0 | 0
6.6 | Performance related pay (PRP) | 17888805 | 19784031 | 10.5945 | Expenditure depend upon the rating of NHPC, KPA and nos of empolyees in the project
| Sub-total (Employee Cost) | 339208057 | 366680351 | 8.099
7 | Loss of Store | 0 | 8638 | 100
|  | 0 | 0
|  | 0 | 0
9.1 | Allocation of CO Office expenses | 133298170 | 242922780 |  | Allocation given by CO
|  | 0 | 0
10 | Others (Specify items) | 28434424 | 31590110 | 11.0981 | Exp. mainly increased on account of dedication of Parbati-III To Nation by Honable P.M in Oct-16 | 3155686
11 | Total (1 to 10) | 745919963 | 933267453
12 | Revenue /Recoveries | 11849373 | 11606595
13 | Net Expenses | 734070590 | 921660858
14 | Capital spares consumed not included in A(1) above and not claimed/allowed by commission for capitalisation