## VSTPP-II2 (2)
VSTPP
| Period | 2002-03 | 2003-04 | 2004-05 | 2005-06 | 2006-07
9 | Cost of spares
9.1 | Cost of spares capitalized in the books (Rs. Lakh) - | 1033.12 | 693.87 |  |  | 713.99
9.2 | Cost of spares included in capital cost for the purpose of tariff (Rs. Lakh) | 582.7 | 534
10 | Generation(MU)
10.1 | Actual Gross Generation at generator terminal | 16931.032 | 16354.01 | 17820.85 | 18304.965 | 19707.981
10.2 | Actual Net Generation Ex-bus | 11692.239 | 15177.36 | 16571.72 | 17013.2 | 18302.31
10.3 | Scheduled Generation Ex-bus | 11626.28 | 15011.34 | 16274.36 | 16765.9 | 18198.57
11 | Average Declared Capacity (DC) (MW) | 1800.8244 | 1760.077 | 1881.6518 | 1940.8527 | 2373.7357
12 | Actual Auxiliary Energy Consumption including colony consumption(MU) | 1185.4072 | 1192.892 | 1247.566 | 1269.236 | 1334.9
13 | Actual Energy supplied to colony from the station (MU)
14 | Main / Primary Fuel
14.1 | Consmption (MT) | 10582131 | 9905724 | 10856904 | 11677761 | 12795406
14.2 | Weighted Average Gross Calorific value (As fired) (kCal/Kg) | 3926 | 4055 | 3986 | 3759 | 3684
14.3 | Weighted Average Price (Rs / Kg) | 972.59 | 1022.4 | 1108.82 | 1138.57 | 1237.12
14.4 | Actual Average stock maintained (MT) | 443384 | 649104 | 296130 | 261182 | 283119
14.5 | Actual Transit & Handling Losses for coal (%) | 0.193 | 0.227 | 0.176 | 0.15 | 0.216
15 | Secondary Fuel
15.1 | Consumption (KL) | 3624.64 | 2970.66 | 2767.35 | 2786.78 | 2712.56
15.2 | Weighted Average Gross Calorific value (As fired) (kCal/L) | 9982 | 9759 | 9730 | 9731 | 9732
15.3 | Weighted Average Price (Rs. Per MT or KL) | 12613.62 | 15547.2 | 15894.37 | 18355.48 | 23433.27
15.4 | Actual Average stock maintained (MT or KL) | 5085 | 3886 | 4014 | 4732 | 6140
16 | Weighted Average duration of outages
16.1 | Scheduled Outages (Days) | 32.56 | 8.91 | 30.54 | 16.18 | 23.22
16.2 | Forced Outages (Days) | 8.9 | 44.51 | 4.1 | 10.67 | 5.07
17 | Cost of spares consumed in Rs.Lakhs | 4375.39 | 3727.64 | 4735.34 | 4674.45 | 5832.91
18 | Average stock of spares in Rs.Lakh | 10554.86 | 10387.46 | 10410.14 | 10179.29 | 11648.79
19 | Number of employees deployed in O & M
19.1 | Executives | 372 | 361 | 338 | 394 | 407
19.2 | Non Executive | 760 | 760 | 743 | 738 | 718

## VSTPP-II1 (2)
Actual anuual performance/operational data for the coal based thermal generating satations
for the 5-year period from 2002-03 to 2006-07.
1 | Name of the Company | NTPC Ltd.
2 | Name of the Station | Vindhyachal Super Thermal Power Sation
3 | Installed Capacity(MW) and Configuration | (210 MW x 6 + 500 MW x 2 + 500 MW x 2 =3260 MW)
4 | Rated Steam Parameters(Type of Steam turbine and Boiler) | 130 Ksc / 535C / 641.8 TPH (LMZ / corner Fired Russian Boiler )-- ST-I / 170 Ksc/537C/ 1498.0 TPH (KWU/BHEL) ST II & III
5 | Type of BFP | Electro driven ST-I / Turbo Driven ST -II & III
6 | Circulating water system | closed cycle
7 | Any other Site specific feature | Nil
8 | Fuels
8.1 | Main Fuel | coal
8.1.1 | Annual Allocation/Requirement | 17.5 MT (for all the three stage)
8.1.2 | Sources of supply | Nigahi/Dudhichua/CCL
8.1.3 | Distance of the station from the sources of supply | 19.6 KM
8.1.4 | Mode of Transport | MGR / Rails
8.1.5 | Maximum Station capability to stock main fuel | 10 Lakh MT for Stage I, II & III
8.2 | Secondary Fuel | HFO & LDO
8.2.1 | Annual Allocation/Requirement | 5000 KL (for all the three stage)
8.2.2 | Sources of supply | IOC, Haldia Refinery/Bitoni Jabalpur
8.2.3 | Distance of the station from the sources of supply | 1000 KM / 400 KM (approx.)
8.2.4 | Mode of Transport | Rails / Road
8.2.5 | Maximum Station capability to stock secondary fuel | 8938 KL (for all three stage)

## TANDA2
Actual anuual performance/operational data for the coal based thermal generating satations
for the 5-year period from 2002-03 to 2006-07.
|  |  | 2002-03 | 2003-04 | 2004-05 | 2005-06 | 2006-07
1 | Name of the Company | NTPC
2 | Name of the Station | TANDA
3 | Installed Capacity(MW) and Configuration | 440 MW
4 | Rated Steam Parameters(Type of Steam turbine and Boiler) | Pr/Tempr. | 535°C/130Kg/cm2
5 | Type of BFP | Electrical Driven
6 | Circulating water system | Closed Cycle
7 | Any other Site specific feature
8 | Fuels
8.1 | Main Fuel | Coal
8.1.1 | Annual Allocation/Requirement | MT | 1994773 | 2329617 | 2595357 | 2567858 | 2670137
8.1.2 | Sources of supply |  | ECL/CCL/BCCL
8.1.3 | Distance of the station from the sources of supply |  | 650 KMS
8.1.4 | Mode of Transport |  | Rail
8.1.5 | Maximum Station capability to stock main fuel | Lacs MT | 2.5
8.2 | Secondary Fuel |  | LDO
8.2.1 | Annual Allocation/Requirement | KL | 4709 | 2870 | 2443 | 2061 | 1410
8.2.2 | Sources of supply |  | IOC
8.2.3 | Distance of the station from the sources of supply |  | 300 KMS
8.2.4 | Mode of Transport |  | RAIL
8.2.5 | Maximum Station capability to stock secondary fuel (KL) |  | 4000KL

## Tanda 3
TANDA
| Period |  | 2002-03 | 2003-04 | 2004-05 | 2005-06 | 2006-07
9 | Cost of spares
9.1 | Cost of spares capitalized in the books (Rs. Lakh) | Rs Lacs | 183.29 | 256.39 | 306.22 | 145.13
9.2 | Cost of spares included in capital cost for the purpose of tariff (Rs. Lakh) | Rs Lacs | 183.29 | 256.39
10 | Generation(MU)
10.1 | Actual Gross Generation at generator terminal |  | 2219.196 | 2911.13 | 3317.58 | 3329.971 | 3512.861
10.2 | Actual Net Generation Ex-bus |  | 1912.08 | 2536.2 | 2919.56 | 2034.32 | 3114.337
10.3 | Scheduled Generation Ex-bus |  | NA | NA | NA | 836.128 | 3084.52
11 | Average Declared Capacity (DC) (MW) |  | NA | NA | NA |  | 356
12 | Actual Auxiliary Energy Consumption including colony consumption(MU) |  | 299.12 | 393.13 | 398.01 | 396.651 | 308.525
13 | Actual Energy supplied to colony from the station (MU)
14 | Main Fuel - Coal
14.1 | Consmption (MT) | MT | 1994773 | 2329617 | 2595357 | 2567858 | 2670137
14.2 | Weighted Average Gross Calorific value (As fired) (kCal/Kg) |  | 3467 | 3545 | 3516 | 3562 | 3612
14.3 | Weighted Average Price (Rs/MT) |  | 1438.59 | 1404.82 | 1653.32 | 1682.92 | 1809.89
14.4 | Actual Average stock maintained (MT) |  | 101641.7 | 45897.52 | 44163.51 | 130425.6 | 176566.2
14.5 | Actual Transit & Handling Losses for coal/Lignite (%) |  | 0.42 | 0.57 | 0.49 | 0.52 | 0.40
15 | Secondary Fuel Oil | LDO
15.1 | Consumption (MT/KL) | kl | 4709 | 2870 | 2443 | 2061 | 1410
15.2 | Weighted Average Gross Calorific value (As fired) (kCal/L) |  | 9621 | 9601 | 9601 | 9600 | 9600
15.3 | Weighted Average Price (Rs. Per MT or KL) |  | 14506.37 | 15516 | 20645.69 | 26468.5 | 30226.09
15.4 | Actual Average stock maintained (MT or KL) |  | 2558 | 2248 | 2203 | 2358 | 2109
16 | Weighted Average duration of outages
16.1 | Scheduled Outages (Days) |  | 88.351 | 48.868 | 28.105 | 34.594 | 28.434
16.2 | Forced Outages (Days) |  | 31.430 | 10.856 | 4.988 | 11.303 | 8.728
17 | Cost of spares consumed in Rs.Lakhs |  | 1315.38 | 1806.91 | 1575.74 | 1310 | 1207.59
18 | Average stock of spares in Rs.Lakh |  | 1038.695 | 1340.2825 | 1406.7825 | 1548.13 | 1873.3975
19 | Number of employees deployed in O & M
19.1 | Executives |  | 153 | 162 | 161 | 160 | 161
19.2 | Non Executive |  | 256 | 250 | 236 | 225 | 220

## Kawas 1
Actual anuual performance/operational data for the coal based thermal generating satations
for the 5-year period from 2002-03 to 2006-07.
1 | Name of the Company | NTPC Ltd.
2 | Name of the Station | Kawas Gas Power Station
3 | Installed Capacity(MW) and Configuration | 4 x 106 MW Gas turbine + 2 X 116.1 MW Steam Turbine = 656.2 MW
4 | Make of Turbine | Gas Turbine : European Gas Turbine, France. Steam Turbine : GEC Alsthom
5 | Rated Steam Parameters(Type of Steam turbine and Boiler) | 67 bars, 517.6 deg C
6 | Average site ambient consitions | 27 deg C, 1.013 bars, 60% RH
7 | Any other Site specific feature | Temperature variation from 8 deg C to 38 deg C
8 | Fuels
8.1 | Main Fuel | Natural Gas / RLNG/ LNG
8.1.1 | Annual Allocation/Requirement MSCM | 1095
8.1.2 | Sources of supply | GAIL, HLPL, GSPC
8.1.3 | Distance of the station from the sources of supply | GAIL - 12 Km, HLPL - 20 Km, GSPC - 2 Km
8.1.4 | Mode of Transport | PIPELINES
8.1.5 | Maximum Station capability to stock main fuel | NIL
8.2 | Secondary Fuel | NAPHTHA/NGL
8.2.1 | Annual Allocation/Requirement | 1009.152
8.2.2 | Sources of supply | HPCL
8.2.3 | Distance of the station from the sources of supply | 12 Kms
8.2.4 | Mode of Transport | PIPELINES
8.2.5 | Maximum Station capability to stock secondary fuel -KL | 5760

## Kawas 2
KAWAS
| Period | 2002-03 | 2003-04 | 2004-05 | 2005-06 | 2006-07
9 | Cost of spares
9.1 | Cost of spares capitalized in the books (Rs. Lakh) | 370.16 | 3845.83
9.2 | Cost of spares included in capital cost for the purpose of tariff (Rs. Lakh) | 0.0 | 0.0
10 | Generation(MU)
10.1 | Actual Gross Generation at generator terminal
10.1.1 | Total | 4203.196 | 3888.706 | 2822.395 | 2884.321 | 3628.74198
10.1.2 | On Gas
10.1.3 | On Naphtha or any other liquid fuel
10.2 | Actual Net Generation Ex-bus | 4129.015 | 3802.421 | 2754.778 | 2821.097 | 3565.698
10.3 | Scheduled Generation Ex-bus | 4079.883 | 3837.94 | 2815.705 | 2834.282 | 3632.010
11 | Average Declared Capacity (DC) (MW) | 521.7 | 558.8 | 582.3 | 589.4 | 602.3
12 | Actual Auxiliary Energy Consumption including colony consumption(MU) | 74.181 | 86.285 | 67.617 | 63.124 | 63.044
13 | Actual Energy supplied to colony from the station (MU)
14 | Main / Primary Fuel
14.1 | Consmption (MSCM) | 274.63981 | 233.931022 | 60.214877 | 339.5134651 | 623.4602699
14.2 | Weighted Average Gross Calorific value (As fired) (kCal/Kg) | 9938 | 9955 | 9946 | 9971 | 9773
14.3 | Weighted Average Price (Rs per 1000 SMC) | 4838.75 | 4786.35 | 4573.95 | 5720.08 | 17223.03
14.4 | Actual Average stock maintained (MT) | NIL | NIL | NIL | NIL | NIL
15a | Alternate Fuel (NAPHTHA)
15a.1 | Consumption (KL) | 500781.720 | 487605.123 | 445458.392 | 212674.651 | 98723.766
15a.2 | Weighted Average Gross Calorific value (As fired) (kCal/L) | 11301 | 11307 | 11316 | 11314 | 11307
15a.3 | Weighted Average Price (Rs. Per MT or KL) | 16913.62 | 17517.39 | 23087.44 | 33013.59 | 37020.17
15a.4 | Actual Average stock maintained (MT or KL) | 5997.87 | 5619.01 | 4705.147 | 6010.58 | 6029.85
15b | Alternate Fuel (HSD)
15b.1 | Consumption (KL) | 764.961 | 601.320 | 693.046 | 674.235 | 647.025
15b.2 | Weighted Average Gross Calorific value (As fired) (kCal/L) | 10935 | 10935 | 10933 | 10836 | 10929
15b.3 | Weighted Average Price (Rs. Per MT or KL) | 19757.64 | 21739.37 | 25566.47 | 30998.55 | 34459.09
15b.4 | Actual Average stock maintained (MT or KL) | 285.596 | 301.448 | 287.254 | 257.679 | 269.128
16 | Weighted Average duration of outages
16.1 | Scheduled Outages (Days) | 9.09 | 8.02 | 11.86 | 7.3 | 7.01
16.2 | Forced Outages (Days) | 15.26 | 4.14 | 0.73 | 0.62 | 0.15
17 | 67767 | 3621.54 | 2497.95 | 3923.75 | 1614 | 1049.5
18 | Average stock of spares in Rs. Lakh | 4896.84 | 4473.96 | 4315.51 | 4278.58 | 4182.98
19 | Number of employees deployed in O & M
19.1 | Executives | 59 | 65 | 59 | 76 | 66
19.2 | Non-Executives | 93 | 88 | 87 | 87 | 87

## Korba2
Actual anuual performance/operational data for the coal based thermal generating satations
for the 5-year period from 2002-03 to 2006-07.
1 | Name of the Company | NTPC Ltd.
2 | Name of the Station | Korba Super Thermal Power Sation
3 | Installed Capacity(MW) and Configuration | 2100 MW (200*3 + 500*3)
4 | Rated Steam Parameters(Type of Steam turbine and Boiler) | BHEL make (CE Design) Boiler, KWU (Germany) make, 3 cylinder Reheat condensing Turbine. Steam parameters Pressure 150/170 ksc, Temp 535/537 deg C, Flow 603/1530 MT/Hrs for 200/500 MW units
5 | Type of BFP | Electrical Driven or Steam driven
6 | Circulating water system | closed cycle
7 | Any other Site specific feature
8 | Fuels
8.1 | Main Fuel | coal
8.1.1 | Annual Allocation/Requirement | 12.32 MMT Requirement
8.1.2 | Sources of supply | Gevra mines - SECL
8.1.3 | Distance of the station from the sources of supply | Around 17 km
8.1.4 | Mode of Transport | MGR
8.1.5 | Maximum Station capability to stock main fuel | 500000MTs
8.2 | Secondary Fuel | HFO & HSD
8.2.1 | Annual Allocation/Requirement | 4250 kl
8.2.2 | Sources of supply | HFO from IOC Haldia (WB) and HSD from IOC Bilaspur depot
8.2.3 | Distance of the station from the sources of supply | HFO around 850 km & HSD around 100 km
8.2.4 | Mode of Transport | HFO by Rail & HSD by Road
8.2.5 | Maximum Station capability to stock secondary fuel | 16700 KL (HFO) & 400 KL (HSD)

## Korba3
KORBA
| Period | 2002-03 | 2003-04 | 2004-05 | 2005-06 | 2006-07
9 | Cost of spares
9.1 | Cost of spares capitalized in the books (Rs. Lakh) | 1384.93 | 819.95 | 437.93 | 109.6
9.2 | Cost of spares included in capital cost for the purpose of tariff (Rs. Lakh) | nil | nil
10 | Generation(MU)
10.1 | Actual Gross Generation at generator terminal | 16460.815 | 16331.686 | 17049.527 | 16001.275 | 16500.068
10.2 | Actual Net Generation Ex-bus | 15448.356 | 15240.069 | 15925.269 | 14957.983 | 15491.621
10.3 | Scheduled Generation Ex-bus | 15328.472 | 15199.611 | 15728.825 | 14791.991 | 15352.766
11 | Average Declared Capacity (DC) (MW) | 1754 | 1738 | 1798 | 1693 | 1753
12 | Actual Auxiliary Energy Consumption including colony consumption(MU) | 1012.459 | 1091.617 | 1124.258 | 1043.292 | 1008.447
13 | Actual Energy supplied to colony from the station (MU)
14 | Main / Primary Fuel
14.1 | Consmption (MT) | 11464750 | 11777546 | 12387697 | 11627076 | 11787158
14.2 | Weighted Average Gross Calorific value (As fired) (kCal/Kg) | 3460 | 3352 | 3304 | 3273 | 3319
14.3 | Weighted Average Price (Rs per MT) | 527.21 | 536.86 | 594.48 | 628.8 | 641.26
14.4 | Actual Average stock maintained (MT) | 272678 | 367684 | 266568 | 346038 | 629059
14.5 | Actual Transit & Handling Losses for coal/Lignite (%) | 0.122 | 0.099 | 0.017 | 0.117 | 0.281
15 | Secondary Fuel
15.1 | Consumption (KL) | 3998.5 | 3435 | 1835.5 | 1773 | 1609.5
15.2 | Weighted Average Gross Calorific value (As fired) (kCal/L) | 10088 | 10156 | 10179 | 10174 | 10180
15.3 | Weighted Average Price (Rs. Per MT or KL) | 12507.47 | 14157.56 | 15847.75 | 20141.65 | 21722.8
15.4 | Actual Average stock maintained (MT or KL) | 4221 | 4044 | 4004 | 4001 | 3435
16 | Weighted Average duration of outages
16.1 | Scheduled Outages (Days) | 21.2 | 26.9 | 19.4 | 21.8 | 39.2
16.2 | Forced Outages (Days) | 4.9 | 3.3 | 4.8 | 26.8 | 3.9
17 | Cost of Spares actually Consumed - in Rs. Lakhs | 4740.18 | 4414.5 | 3865.84 | 4136.62 | 3562.79
18 | Average stock of spares - in Rs. Lakhs | 7860 | 8193.96 | 8586.04 | 8820.15 | 9430.74
19 | Number of employees deployed in O & M
19.1 | Executives | 320 | 310 | 306 | 311 | 305
19.2 | Non-Executives | 1104 | 1049 | 1033 | 989 | 952

## Farakka2
Actual anuual performance/operational data for the coal based thermal generating satations
for the 5-year period from 2002-03 to 2006-07.
1 | Name of the Company | NTPC Ltd.
2 | Name of the Station | Farakka Super Thermal Power Sation,
3 | Installed Capacity(MW) and Configuration | 3 X 200 MW0+ 2 X 500 MW
|  | 200 MW - Unit ; MS and HRH 535°C | 500 MW unit : MS and HRH 537°C,
4 | Rated Steam Parameters(Type of Steam turbine and Boiler) | Boiler : tagential fired, natural circulation, Turbine : Single reheat, regenerative, 3 cylinder reaction turbine | Boiler : oppposed fired, natural circulation, Turbine : Single reheat, regenerative, 3 cylinder reaction turbine
2 Nos. Steam Turbine driven and 1 No. motor driven for 500 MW units
5 | Type of BFP | Motor driven for 200 MW units
6 | Circulating water system | open cycle
7 | Any other Site specific feature | Circulating water drawn from feeder canal
8 | Fuels
8.1 | Main Fuel | coal
8.1.1 | Annual Allocation/Requirement | Annual requirement is about 11 MMT
8.1.2 | Sources of supply | Lalmatia (ECL), CCL, MCL, BCCL, NEC, ECL (ASANSOL), ECL (Raniganj) and imported
8.1.3 | Distance of the station from the sources of supply | MGR length to Lalmatia is about 86 km from station
8.1.4 | Mode of Transport | Rails & MGR
8.1.5 | Maximum Station capability to stock main fuel | Approx. 7.5 lac MT
8.2 | Secondary Fuel | HFO
8.2.1 | Annual Allocation/Requirement | Approx. 20730 KL
8.2.2 | Sources of supply | IOC
8.2.3 | Distance of the station from the sources of supply | 350 km approx.
8.2.4 | Mode of Transport | Rails
8.2.5 | Maximum Station capability to stock main fuel | 10700 KL approx.

## Farakka3
FARRAKKA
| Period | 2002-03 | 2003-04 | 2004-05 | 2005-06 | 2006-07
9 | Cost of spares (Rs. Lakh)
9.1 | Cost of spares capitalized in the books (Rs. Lakh) | 1087.96 | 1300.14 | 171.12 | 764.55
9.2 | Cost of spares included in capital cost for the purpose of tariff (Rs. Lakh) | Nil | Nil | Nil | Nil
10 | Generation(MU)
10.1 | Actual Gross Generation at generator terminal (MU) | 8948.35 | 9487.51 | 9700.59 | 11463.87 | 11399.02
10.2 | Actual Net Generation Ex-bus (MU) | 8231.12 | 8713.36 | 8876.39 | 10660.96 | 10639.07
10.3 | Scheduled Generation Ex-bus (MU) | N.A. | 8577.47 | 8828.48 | 10515.41 | 10450.62
11 | Average Declared Capacity (DC) (MW) | N.A. | 1032.17 | 1043.11 | 1247.36 | 1255.99
12 | Actual Auxiliary Energy Consumption including colony consumption(MU) | 717.23 | 774.14 | 824.2 | 802.91 | 759.96
13 | Actual Energy supplied to colony from the station (MU)
14 | Main Fuel | COAL | COAL | COAL | COAL | COAL
14.1 | Consmption (MT) | 7576126 | 8833241 | 8934468 | 9441561 | 9625056
14.2 | Weighted Average Gross Calorific value (As fired) (kCal/Kg) | 2902 | 2642 | 2722 | 2954 | 2872
14.3 | Weighted Average Price (Rs/MT) | 964.41 | 933.12 | 1071.30 | 1330.64 | 1219.58
14.4 | Actual Average stock maintained (MT) | 551816 | 123495 | 94854 | 304470 | 633277
14.5 | Actual Transit & Handling Losses for coal/Lignite (%) | 0.35 | 0.58 | 0.33 | 0.34 | 0.28
15 | Secondary Fuel Oil | HFO | HFO | HFO | HFO | HFO
15.1 | Consumption (MT/KL) | 15895.86 | 18404.15 | 23455.79 | 10771.00 | 10214.50
15.2 | Weighted Average Gross Calorific value (As fired) (kCal/L) | 9469 | 9574 | 9577 | 9579 | 9578
15.3 | Weighted Average Price (Rs. Per MT or KL) | 12358.01 | 13546.64 | 14471.33 | 17596.12 | 24036.54
15.4 | Actual Average stock maintained (MT or KL) | 5587.6 | 5671.7 | 4163.4 | 4949.1 | 4106.7
16 | Weighted Average duration of outages
16.1 | Scheduled Outages (Days) | 34.68 | 27.19 | 30.05 | 24.90 | 28.99
16.2 | Forced Outages (Days) | 46.65 | 37.15 | 30.85 | 16.10 | 19.56
17 | Cost of Spares actually Consumed - Capital in Rs.Lakh | 365.74 | 497.93 | 415.63 | 544.02 | 375.67
18 | Average stock of spares in Rs.Lakh | 12245.43 | 11420.84 | 10636.41 | 12263.01 | 13948.95
19 | Number of employees deployed in O & M
19.1 | Executives | 317 | 327 | 306 | 325 | 312
19.2 | Non-Executives | 780 | 775 | 754 | 741 | 734

## BTPS 1
Performa for furnishing Actual Annual Performance / Operational data for the Coal based thermal generating stations for the 5 year period from 2002-03 to 2006-07
1 | Name of the Company | NTPC Ltd.
2 | Name of the Station | Badarpur Thermal Power Station
3 | Installed Capacity(MW) and Configuration | 705 MW - 95 MW X 3 + 210 MW X 2
4 | Rated steam parameters (Also state the tyoe of Steam turbine and Boiler) | 95 MW - 90.0 Kg/cm2, 535 Deg C
210 MW - 130.0 Kg/cm2, 535 Deg C
5 | Type of BFP | MDBFP
6 | Circulating water system | Open cycle system/Closed cycle system
7 | Any other Site specific feature | Cooling Towers are inadequate
8 | Fuels
8.1 | Main/Primary Fuel | Coal
8.1.1 | Annual Allocation/Requirement | 48,00,000 MT
8.1.2 | Sources of supply | BCCL, ECL, CCL
8.1.3 | Distance of the station from the sources of supply | 1200 KM approx.
8.1.4 | Mode of Transport | RAIL
8.1.5 | Maximum Station capability to stock main fuel | 4,00,000 MT
8.2 | Secondary Fuel | LDO
8.2.1 | Annual Allocation/Requirement | 2700 KL
8.2.2 | Sources of supply | IOC, BRPL
8.2.3 | Distance of the station from the sources of supply | 200 KM / 500 KM
8.2.4 | Mode of Transport | RAIL
8.2.5 | Maximum Station capability to stock secondary fuel | 6450 KL

## BTPS 2
BTPS
| Period | 2002-03 | 2003-04 | 2004-05 | 2005-06 | 2006-07
9 | Cost of spares
9.1 | Cost of spares capitalized in the books (Rs. Lakh) | 2389 | 287 | 184 | 1478 | 649
9.2 | Cost of spares included in capital cost for the purpose of tariff (Rs. Lakh)
10 | Generation(MU)
10.1 | Actual Gross Generation at generator terminal | 5279.833 | 5428.992 | 5462.593 | 5380.437 | 5306.430
10.2 | Actual Net Generation Ex-bus | 4796.6206 | 4903.302 | 4968.506 | 4905.058 | 4879.453
10.3 | Scheduled Generation Ex-bus |  |  |  | 4871 | 4853
11 | Average Declared Capacity (DC) (MW) |  |  |  | 574 | 567
12 | Actual Auxiliary Energy Consumption excluding colony consumption(MU) | 526.2845 | 554.296 | 546.166 | 514.7676 | 502.9261
13 | Actual Energy supplied to colony from the station (MU)
14 | Main / Primary Fuel | Coal
14.1 | Consmption (MMSCM) | 3547503 | 3581307 | 3781294 | 3712488 | 3735265
14.2 | Weighted Average Gross Calorific value (As fired) (kCal/Kg) | 4166 | 4224 | 4023 | 4002 | 3903
14.3 | Weighted Average Price (Rs per MT) | 2172 | 2192 | 2158 | 2415 | 2536
14.4 | Actual Average stock maintained (MT) | 149551 | 112723 | 113338 | 296322 | 240800
14.5 | ACTUAL Transit & Handling losses for coal (%)* | 0.55 | 0.55 | 0.56 | 0.57 | 0.69
15 | Secondary Fuel Oil | LDO | LDO | LDO | LDO | LDO
15.1 | Consumption (KL) | 2216 | 1646 | 1787 | 1802.5 | 2219.5
15.2 | Weighted Average Gross Calorific value (As fired) (kCal/L) | 9670 | 9654 | 9659 | 9650 | 9651
15.3 | Weighted Average Price (Rs. Per MT or KL) | 13888 | 15970 | 16905 | 20065 | 24728
15.4 | Actual Average stock maintained (MT or KL)** | 2065 | 1933 | 1504 | 1574 | 1573
16 | Weighted Average duration of outages
16.1 | Scheduled Outages (Days) | 19.82 | 14.32 | 17.4 | 28.7 | 29.4
16.2 | Forced Outages (Days) | 8.8 | 0.9 | 9.37 | 6.2 | 11.9
17 | Cost of Spares actually Consumed - Capital in Rs.Lakh | 2341 | 2869 | 1864 | 3373 | 3254
18 | Average stock of spares in Rs.Lakh | 6283 | 5584 | 5853 | 5581 | 5128
19 | Number of employees deployed in O & M
19.1 | Executives | 345 | 344 | 359 | 366 | 351
19.2 | Non-Executives | 1547 | 1439 | 1343 | 1268 | 1190

## Ramagundam I&II-2(2)
Ramagundam
|  | 2002-03 | 2003-04 | 2004-05 | 2005-06 | 2006-07
9 | Cost of spares
9.1 | Cost of spares capitalized in the books (Rs. Lakh) | 3320.92 | 1201.67 | 1328.5 | 704.19
9.2 | Cost of spares included in capital cost for the purpose of tariff (Rs. Lakh) | 0 | 0 | 1169
10 | Generation(MU)
10.1 | Actual Gross Generation at generator terminal | 16836.714 | 16331.779 | 16725.786 | 19690.837 | 20247.702
10.2 | Actual Net Generation Ex-bus | 15743.1119 | 15248.3525 | 15573.353 | 18431.578 | 18989.437
10.3 | Scheduled Generation Ex-bus | - | 15105.0286 | 15358.071 | 18196.998 | 18748.302
11 | Average Declared Capacity (DC) (MW) | - | 1747.33 | 2243.887 | 2207.163 | 2196.464
12 | Actual Auxiliary Energy Consumption including colony consumption(MU) | 1091.6548 | 1079.6005 | 1103.9413 | 1259.2587 | 1258.2655
13 | Actual Energy supplied to colony from the station (MU)
14 | Main Fuel
14.1 | Consmption (MT) | 10439081 | 10139243 | 10096830 | 11778688 | 12503168
14.2 | Weighted Average Gross Calorific value (As fired) (kCal/Kg) | 3934 | 3929 | 4014(Stage I & II) 3908(Stage III) | 4079(Stage I & II) 3764(stage III) | 3898 (Stage I & II ) 3639 ( Stage III)
14.3 | Weighted Average Price (Rs/MT) | 1164.7 | 1168.91 | 1231.34 ( Stage I & II) 1320.35 ( stage III) | 1335.58(Stage I & II) 1349.53( Stage III) | 1350.3 ( Stage I & II) 1372.17 ( Stage III)
14.4 | Actual Average stock maintained (MT) | 465833 | 369683.5 | 422804.115 | 475337.115 | 522701.5
14.5 | Actual Transit & Handling Losses for coal/Lignite (%) | 0.473 | 0.214 | 0.206 | 0.228 | 0.231
15 | Secondary Fuel Oil
15.1 | Consumption (KL) | 3584.512 | 3828.164 | 2845.125 | 4725.178 | 3824.075
15.2 | Weighted Average Gross Calorific value (As fired) (kCal/L) | 9657 | 9709 | 9558 ( Stage I&II ) 10111 ( Stage III ) | 9780 (Stage I & II ) 10172 ( stage III ) | 9887 (Stage I & II ) 10065 (stage III )
15.3 | Weighted Average Price (Rs. Per KL) | 14224.57 | 17183.32 | 21596.34 (Stage I & II ) 17077.57 (Stage III ) | 25398.91(Stage I & II) 20985.62(Stage III ) | 25803.4 (Stage I & II ) 24259.35 (Stage III )
15.4 | Actual Average stock maintained (KL) | 2191.989 | 1251.219 | 1044.113 | 1210.916 | 1342.769
16 | Weighted Average duration of outages
16.1 | Scheduled Outages (Days) | 17.48 | 25.31 | 26.94 | 28.18 | 19.89
16.2 | Forced Outages (Days) | 9.12 | 7.71 | 5.92 | 4.86 | 14.52
17 | Cost of spares consumed in Rs.Lakh | 3633 | 5318 | 3348 | 4835 | 6824
18 | Average stock of spares in Rs.Lakhs | 10411 | 9293 | 9810 | 10898 | 11043
19 | Number of employees deployed in O & M
19.1 | Executives | 516 | 498 | 509 | 520 | 538
19.2 | Non Executives | 1236 | 1221 | 1195 | 1163 | 1123

## Ramagundam 1(2)
Actual anuual performance/operational data for the coal based thermal generating satations
for the 5-year period from 2002-03 to 2006-07.
|  | Stage 1 & 2 | Stage 3
|  | (3x200 + 3x500 MW) | (1x500 MW)
1 | Name of the Company | NTPC Ltd.
2 | Name of the Station | Ramagundam Super Thermal Power Station
3 | Installed Capacity(MW) and Configuration | 2100 MW (3X200+3X500) | 500 mw (1X500)
4 | Rated Steam Parameters(Type of Steam turbine and Boiler) | 537/150/670 (200MW) and 540/170/1725 (500 MW) Deg C/ksc/BMCR Stm flow | 540/170/1675 (500MW) Deg C/ksc/BMCR Stm flow
5 | Type of BFP | Stage 1 : 3x50% Electrical driven BFP | 2x50% Steam driven BFPs and 1 x50% electrical BFP
Stage 2 : 2x50% Steam driven BFPs and 1x50% Electrical BFP
6 | Circulating water system | Closed cycle | Closed cycle
7 | Any other Site specific feature
8 | Fuels | COAL, HFO,HSD | COAL, HFO, LDO
8.1 | Main Fuel | COAL | COAL
8.1.1 | Annual Allocation/Requirement( Lakh MT) | 135.93
8.1.2 | Sources of supply | SCCL | SCCL, SECL, MCL, WCL
8.1.3 | Distance of the station from the sources of supply | SCCL : OC 1&2 - 15 kms. OC 3 12 kms, RKP - 25 kms, SRP - 20 Kms., Manguru - 310 Kms SECL :Gevra -789 Kms; MCL : Belapahar - 876 Kms ; WCL : Ghughus - 190 Kms , wni 212 Kms , Mairi - 205 Kms
8.1.4 | Mode of Transport | MGR & RAIL | RAIL
8.1.5 | Maximum Station capability to stock main fuel (MT) | 7,50,000
8.2 | Secondary Fuel | HFO, HSD | HFO, HSD
8.2.1 | Annual Allocation/Requirement | - | -
8.2.2 | Sources of supply | IOCL | IOCL
8.2.3 | Distance of the station from the sources of supply | HSD 140 km and HFO 650- km (approx)
8.2.4 | Mode of Transport | rail / road
8.2.5 | Maximum Station capability to stock secondary fuel (KL) | 20714

## Kahalgaon 2
KAHALGAON
| Period | 2002-03 | 2003-04 | 2004-05 | 2005-06 | 2006-07
9 | Cost of spares
9.1 | Cost of spares capitalized in the books (Rs. Lakh) | 1361.23 | 226.18 | 139.33 | 437.33
9.2 | Cost of spares included in capital cost for the purpose of tariff (Rs. Lakh) | 679
10 | Generation(MU)
10.1 | Actual Gross Generation at generator terminal | 4990.0935 | 5966.9819 | 6082.2553 | 6572.2734 | 6579.4685
10.2 | Actual Net Generation Ex-bus | 4513.1423 | 5391.8545 | 5542.2003 | 6013.0461 | 6014.7161
10.3 | Scheduled Generation Ex-bus |  | 5298.129 | 5467.788 | 5800.397 | 5921.272
11 | Average Declared Capacity (DC) (MW) |  | 645 | 643 | 701 | 701
12 | Actual Auxiliary Energy Consumption including colony consumption(MU) | 476.9512 | 575.0265 | 536.2181 | 552.5725 | 548.9005
13 | Actual Energy supplied to colony from the station (MU)
14 | Main Fuel | Coal
14.1 | Consmption (MT) | 4528281 | 5429733 | 5520235 | 5831194 | 5574807
14.2 | Weighted Average Gross Calorific value (As fired) (kCal/Kg) | 2726 | 2698 | 2697 | 2750 | 2864
14.3 | Weighted Average Price (Rs/MT) | 981.75 | 998.93 | 1135.8 | 1239.10 | 1322.35
14.4 | Actual Average stock maintained (MT) | 238779 | 37499 | 78422 | 251170 | 360286
14.5 | Actual Transit & Handling Losses for coal/Lignite (%) | 0.226 | 0.212 | .146 | 0.209 | 0.261
15 | Secondary Fuel Oil | HFO
15.1 | Consumption (MT/KL) | 3167.76 | 3250.45 | 3233.49 | 2719.51 | 4032.49
15.2 | Weighted Average Gross Calorific value (As fired) (kCal/kg or L) | 9840 | 9861 | 9935 | 9927 | 9970
15.3 | Weighted Average Price (Rs. Per MT or KL) | 12656.99 | 14183.91 | 15546.75 | 19751.29 | 21144.65
15.4 | Actual Average stock maintained (MT or KL) | 2967.68 | 2543.06 | 2100.86 | 2266.71 | 2312.82
16 | Weighted Average duration of outages
16.1 | Scheduled Outages (Days) | 20.15 | 25.05 | 24.17 | 18.17 | 23.53
16.2 | Forced Outages (Days) | 33.76 | 10.79 | 6.94 | 6.68 | 4.95
17 | Cost of spares consumed in Rs.Lakh | 2006.7 | 1860.59 | 1908.26 | 2823.73 | 3137.44
18 | Average stock of spares in Rs.Lakh | 3711.48 | 3267.46 | 3271.69 | 3627.47 | 4484.69
19 | Number of employees deployed in O & M
19.1 | Executives | 225 | 210 | 207 | 274 | 290
19.2 | Non-Executives | 454 | 450 | 436 | 412 | 393

## Kahalgaon 1
Actual anuual performance/operational data for the coal based thermal generating satations
for the 5-year period from 2002-03 to 2006-07.
1 | Name of the Company | NTPC Ltd.
2 | Name of the Station | Kahalgaon Super Thermal Power Sation
3 | Installed Capacity(MW) and Configuration | 840 MW
4 X 210 MW
4 | Rated Steam Parameters(Type of Steam turbine and Boiler) | Boiler TYPE : Natural Circulation, Dry Bottom, Balanced Draft, Convective Reheat : Solid Fuel with Direct, Tangential Fired, Pulverised Fuel system. Rating : MS 690 T/Hr, 140 Kg/Cm2, 540 deg C RH 569 T/Hr 27.6 Kg.Cm2, 328.ºC/540 ºC. Turbine : Type : K-210-130-8, Impulse Reaction, Tandem compound, Re-heat type, Nozzle govering, Closed cycle with regenerative bleeding.
5 | Type of BFP | Electrically driven
6 | Circulating water system | Closed cycle
7 | Any other Site specific feature | Separate Make - Up Water Pump House in the river Ganges for pumping cooling water to the Plant
8 | Fuels
8.1 | Main Fuel | coal - Indian Bituminous Coal of Rajmahal Mines of Eastern Coal Fields Limited.
8.1.1 | Annual Allocation/Requirement | 5.8 MT/Annum
8.1.2 | Sources of supply | Rajmahal Collieries of Eastern Coalfields Limited, Lalmatia. Other Sources : Mahanandi Coalfields Limited, BCCL, CCL, NEC, Coal Imported from Indonesia.
8.1.3 | Distance of the station from the sources of supply | 33 KM for linked mines
8.1.4 | Mode of Transport | MGR, RAIL, Sea
8.1.5 | Maximum Station capability to stock main fuel | 500,000 MT
8.2 | Secondary Fuel | HFO from Haldia Refinery
8.2.1 | Annual Allocation/Requirement | 12000 KL
8.2.2 | Sources of supply | IOC, Haldia Refinery
8.2.3 | Distance of the station from the sources of supply | 521 km approx.
8.2.4 | Mode of Transport | Rails
8.2.5 | Maximum Station capability to stock secondary fuel | 8000 KL

## Talcher Angul 2
TALCHER
| Period | 2002-03 | 2003-04 | 2004-05 | 2005-06 | 2006-07
9 | Cost of spares
9.1 | Cost of spares capitalized in the books (Rs. Lakh) | 633 | 793.45 | 400.75 | 157.58 | 279.58
9.2 | Cost of spares included in capital cost for the purpose of tariff (Rs. Lakh) | 633 | 793
10 | Generation(MU)
10.1 | Actual Gross Generation at generator terminal | 2254.39 | 2738.938 | 3196.496 | 3529.741 | 3550.151
10.2 | Actual Net Generation Ex-bus | 1995.85 | 2445.064 | 2858.412 | 3174.281 | 3188.535
10.3 | Scheduled Generation Ex-bus | 1995.85 | 2445.064 | 2858.412 | 3174.281 | 3167.446
11 | Average Declared Capacity (DC) (MW) | 228 | 278 | 326 | 362 | 362
12 | Actual Auxiliary Energy Consumption including colony consumption(MU) | 258.545 | 293.874 | 338.084 | 355.460 | 361.616
13 | Actual Energy supplied to colony from the station (MU)
14 | Main Fuel
14.1 | Consmption (MT) | 1948265 | 2211844 | 2577585 | 2838028 | 2836370
14.2 | Weighted Average Gross Calorific value (As fired) (kCal/Kg) | 3621 | 3697 | 3617 | 3619 | 3630
14.3 | Weighted Average Price (Rs/MT) | 473.41 | 471.65 | 584.74 | 604.24 | 593.5
14.4 | Actual Average stock maintained (MT) | 50112 | 54613 | 86284 | 295202 | 202585
14.5 | Actual Transit & Handling Losses for coal/Lignite (%) | 0.167 | 0.173 | 0.158 | 0.257 | 0.236
15 | Secondary Fuel Oil
15.1 | Consumption (kL) | 3615.36 | 4258.02 | 2493.81 | 1401.22 | 1547.365
15.2 | Weighted Average Gross Calorific value (As fired) (kCal/L) | 9269 | 9545 | 9468 | 9454 | 9478
15.3 | Weighted Average Price (Rs. Per MT or KL) | 16735.16 | 17673.06 | 21349.15 | 29444.5 | 31122.59
15.4 | Actual Average stock maintained (MT or KL) | 1189 | 1328 | 1158.5 | 1214 | 1210
16 | Weighted Average duration of outages
16.1 | Scheduled Outages (Days) | 93 | 84 | 40 | 17 | 26
16.2 | Forced Outages (Days) | 40 | 15 | 13 | 14 | 12
17 | Cost of spares consumed in Rs.Lakh | 1071.29 | 1361.11 | 1792.73 | 1506.15 | 1715.5
18 | Average stock of spares in Rs.Lakh | 4005.52 | 4090.6 | 4088.54 | 3971.05 | 3863.3
19 | Number of employees deployed in O & M
19.1 | Executives | 144 | 142 | 138 | 140 | 140
19.2 | Non-Executives | 790 | 731 | 691 | 673 | 624

## Talcher Angul 1
Actual anuual performance/operational data for the coal based thermal generating satations
for the 5-year period from 2002-03 to 2006-07.
1 | Name of the Company | NTPC Ltd. | a
2 | Name of the Station | Talcher Thermal Power Sation
3 | Installed Capacity(MW) and Configuration | 460 MW - 4 X 60 MW, Stage-II 2x110 MW
4 | Rated Steam Parameters(Type of Steam turbine and Boiler) | Rated Steam temp at SH O/L 535 deg C, Rated Steam Pressure before stop V/V 130 ata
Stage-I Boiler - Natural circulation, Bi-Drum, Front fired. Steam Turbine - Rated Capacity 62.5 MW, 17 stages, 5 Extraction points, 3000 RPM,.
Stage-II Boiler - Tangentially fired, Balanced draft, Natural circulation, Radiant Reheat type Dry Bottom with Direct fired Pulverised Coal with Bowl Mills. Steam Turbine - Three casing, condensing steam turbine with reheating and non-regulating extraction
5 | Type of BFP | Electrically driven
6 | Circulating water system | Closed cycle
7 | Any other Site specific feature
8 | Fuels
8.1 | Main Fuel | Coal
8.1.1 | Annual Allocation/Requirement | 30,00000 MT
8.1.2 | Sources of supply | MCL
8.1.3 | Distance of the station from the sources of supply | 10 KMS
8.1.4 | Mode of Transport | RAILS, Conveyor
8.1.5 | Maximum Station capability to stock main fuel | 300,000 MT
8.2 | Secondary Fuel | Fuel Oil (LDO, HFO, HSD)
8.2.1 | Annual Allocation/Requirement | HFO - 500 KL, LDO - 500 KL, HSD - 700 KL
8.2.2 | Sources of supply | IOC
8.2.3 | Distance of the station from the sources of supply | 130 kms
8.2.4 | Mode of Transport | Road
8.2.5 | Maximum Station capability to stock secondary fuel | HFO - 2000 KL, LDO - 255 KL, HSD - 255 KL

## Talcher Kaniha-2
Talcher Super TPS
| Period | 2002-03 | 2003-04 | 2004-05 | 2005-06 | 2006-07
9 | Cost of spares
9.1 | Cost of spares capitalized in the books (Rs. Lakh) |  | 2177 | 1507 | 1772.83 | 845.95
9.2 | Cost of spares included in capital cost for the purpose of tariff (Rs. Lakh) |  | 2177 | 1507 | 1143
10 | Generation(MU)
10.1 | Actual Gross Generation at generator terminal | 6438.283 | 9878.104 | 15853.8847 | 20879.0992 | 23656.1328
10.2 | Actual Net Generation Ex-bus |  | 9138.458 | 14773.321 | 19677.75 | 22381.046
10.3 | Scheduled Generation Ex-bus |  | 9067.343 | 14707.66 | 19454.48 | 22196.4
11 | Average Declared Capacity (DC) (MW) |  | 1043 | 1682 | 2282 | 2553
12 | Actual Auxiliary Energy Consumption including colony consumption(MU) | 457.9237 | 692.9696 | 1043.7966 | 1176.3095 | 1301.0836
13 | Actual Energy supplied to colony from the station (MU)
14 | Main Fuel | Coal
14.1 | Consmption (MT) | 4548262 | 7095604 | 11743924 | 13874571 | 16808148
14.2 | Weighted Average Gross Calorific value (As fired) (kCal/Kg) | 3400 | 3350 | 3232 | 3569 | 3329
14.3 | Weighted Average Price (Rs/MT) | 463.39 | 482.19 | 540.36 | 834.04 | 749.75
14.4 | Actual Average stock maintained (MT) | 277960 | 252365 | 94909 | 267509 | 434355
14.5 | Actual Transit & Handling Losses for coal/Lignite (%) | 0.09 (Indian) | 0.03 (Indian) | 0.02(Indian) | 0.08(Indian) 0.04(Imported) | 0.14(Indian 0.05(Imported)
15 | Secondary Fuel Oil | HFO + LDO
15.1 | Consumption (KL) | 2981 | 8156 | 10334 | 10537 | 6398
15.2 | Weighted Average Gross Calorific value (As fired) (kCal/L) | 9500 | 9500 | 9500 | 9500 | 9500
15.3 | Weighted Average Price (Rs. Per KL) | 12741.3 | 14771.08 | 15248.92 | 16886.84 | 21302.25
15.4 | Actual Average stock maintained (MT or KL) | 3304 | 4887 | 5350 | 4893 | 2899
16 | Weighted Average duration of outages
16.1 | Scheduled Outages (Days) | 27.665 | 30.78 | 9.79 | 25.5 | 24.84
16.2 | Forced Outages (Days) | 16.49 | 26.73 | 20.726 | 16.07 | 8.51
17 | Cost of spares consumed in Rs.Lakh | 1665.33 | 2017.41 | 3110.65 | 4237.93 | 6600.01
18 | Average stock of spares in Rs.Lakh | 6507.75 | 8610.01 | 11827.99 | 13074.25 | 14393.76
19 | Number of employees deployed in O & M
19.1 | Executives | 229 | 274 | 306 | 359 | 353
19.2 | Non-Executives | 338 | 350 | 448 | 434 | 423
*

## Talcher Kaniha-1
Actual anuual performance/operational data for the coal based thermal generating satations
for the 5-year period from 2002-03 to 2006-07.
| Period | 2002-03 | 2003-04 | 2004-05 | 2005-06 | 2006-07
1 | Name of the Company | NTPC Ltd.
2 | Name of the Station | Talcher Super Thermal Power Sation (6x500MW)
3 | Installed Capacity(MW) at year end | 1000MW | 2000MW | 2500MW | 3000MW | 3000MW
4 | Rated Steam Parameters(Type of Steam turbine and Boiler) | 170kg/sqcm, 540ºC,
5 | Type of BFP | 2 nos. Steam Driven + 1 stand by motor driven for each unit
6 | Circulating water system | Closed Cycle
7 | Any other Site specific feature
8 | Fuels
8.1 | Main Fuel | Coal
8.1.1 | Annual Allocation/Requirement | 4800000 MT | 8900000 MT | 16320000 MT | 18000000MT | 18750000 MT
8.1.2 | Sources of supply | LINGRAJ OPEN CAST PROJECT OF M/s MAHANADI COALFIELDS | LINGRAJ OPEN CAST PROJECT OF M/s MAHANADI COALFIELDS | LINGRAJ OPEN CAST PROJECT OF M/s MAHANADI COALFIELDS+TALCHER MINES+IB VALLEY+IMPORTED COAL FROM PARADIP PORT
8.1.3 | Distance of the station from the sources of supply | 28 KM | 28 KM | LINGRAJ = 28KM, TALCHER = 47KM, IB VALLEY - 259 & 236 KM, IMPORTED = 201 KM
8.1.4 | Mode of Transport | RAIL
8.1.5 | Maximum Station capability to stock main fuel | 5.0 LAC MT | 5.0 LAC MT | 8.0 LAC MT | 8.0 LAC MT | 8.0 LAC MT
8.2 | Secondary Fuel
8.2.1 | Annual Allocation/Requirement (KL) | 18154 | 30018 | 33048 | 18203 | 6267
8.2.2 | Sources of supply | IOCL, Vizag | IOCL, Vizag | IOCL, Vizag | HPCL, Vizag | HPCL, Vizag
8.2.3 | Distance of the station from the sources of supply | Vizag (612 KM) | Vizag (612 KM) | Vizag (612 KM) | Vizag (612 KM) | Vizag (612 KM)
8.2.4 | Mode of Transport | RAIL
8.2.5 | Maximum Station capability to stock main fuel | 13000 KL | 13000 KL | 13000 KL | 13000 KL | 13000 KL

## Dadri Coal 1
Performa for furnishing Actual Annual Performance / Operational data for the Coal based thermal generating stations for the 5 year period from 2002-03 to 2006-07
1 | Name of the Company | NTPC Ltd.
2 | Name of the Station | NCTPS Dadri
3 | Installed Capacity(MW) and Configuration | 4 x 210 = 840
4 | Rated steam parameters (Also state the tyoe of Steam turbine and Boiler) | Steam parameters capacity 700T/Hr
super heater - Pressure - 154.0 Kg/cm2, Temp - 540 deg C
Reheater Pressure - 38.8 Kg/cm2 Temp. 540 deg C
Boiler Make - BHEL (C.E.Design)
Type - Natural circulation, balanced draft, smooth tube double pass, single drum, single reheat, direct pulverised coal/oil fired, dry bottom type
Turbine - Make BHEL, KRAFTWERK UNION DESIGN
Type - Tandem, compound, regenerative, reheat, condensing, three cylinder having HPT-Reaction, barrel single flow type, IPT - Reaction, Double flowaxially split type, LPT Reaction - double flow three shell design
5 | Type of BFP | Electrical Driven
6 | Circulating water system | Closed Cycle
7 | Any other Site specific feature | Dry ash Handling system
8 | Fuels
8.1 | Main/Primary Fuel | Coal
8.1.1 | Annual Allocation/Requirement | As per norms
8.1.2 | Sources of supply | Ashoka, KDH, RCM and New Bachra coal mines, Jharkhand
8.1.3 | Distance of the station from the sources of supply | 1150 KM (approx.)
8.1.4 | Mode of Transport | Rail
8.1.5 | Maximum Station capability to stock main fuel | 660732 MT
8.2 | Alternative Fuel (HSD)
8.2.1 | Annual Allocation/Requirement | As per norms
8.2.2 | Sources of supply | LDO - DELHI, HFO-MATHURA (UP)
8.2.3 | Distance of the station from the sources of supply | 70 KM for LDO and 200 KM for HFO
8.2.4 | Mode of Transport | Road
8.2.5 | Maximum Station capability to stock secondary fuel | 30360.462 KL

## Dadri Coal 2
DADRI COAL
| Period | 2002-03 | 2003-04 | 2004-05 | 2005-06 | 2006-07
9 | Cost of spares
9.1 | Cost of spares capitalized in the books (Rs. Lakh) | 975.48 | 17.6 | 307.40 | 248.11
9.2 | Cost of spares included in capital cost for the purpose of tariff (Rs. Lakh) | 0.0 | 0.0
10 | Generation(MU)
10.1 | Actual Gross Generation at generator terminal | 6037.97 | 6181.11 | 6831.185 | 6768.10 | 7041.33
10.2 | Actual Net Generation Ex-bus | 5555.230 | 5683.317 | 6329.090 | 6267.829 | 6516.837
10.3 | Scheduled Generation Ex-bus | 5393.568 | 5627.012 | 6173.575 | 6167.176 | 6414.791
11 | Average Declared Capacity (DC) (MW) | 704 | 709 | 735 | 724 | 748
12 | Actual Auxiliary Energy Consumption including colony consumption(MU) | 482.332 | 497.624 | 501.457 | 497.768 | 521.529
13 | Actual Energy supplied to colony from the station (MU)
14 | Main / Primary Fuel | COAL
14.1 | Consmption (MT) | 4047977.7 | 4197046.0 | 4457188.0 | 4317742.0 | 4349991.0
14.2 | Weighted Average Gross Calorific value (As fired) (kCal/Kg) | 3670.7 | 3623.42 | 3728.73 | 3791.8 | 3905.74
14.3 | Weighted Average Price (Rs per MT) | 1945.24 | 1912.62 | 2115.30 | 2214.56 | 2337.43
14.4 | Actual Average stock maintained (MT) | 448404.57 | 289788.78 | 50042.382 | 297589.215 | 330410.547
14.5 | Actual transit and handling losses (%) | 1.115 | 1.164 | 0.517 | 0.657 | 0.603
15 | Secondary Fuel Oil
15.1 | Consumption (KL) | 2629.12 | 1068.01 | 1083.73 | 1427.52 | 757.27
15.2 | Weighted Average Gross Calorific value (As fired) (kCal/L) | 9804.14 | 9799.96 | 9786.4 | 9846.9 | 9842.54
15.3 | Weighted Average Price (Rs. Per MT or KL) | 6974.41 | 7105.22 | 23786.33 | 27056.2 | 29977.37
15.4 | Actual Average stock maintained ( KL) | 16044.866 | 9181.287 | 4863.632 | 3841.904 | 2530.234
16 | Weighted Average duration of outages
16.1 | Scheduled Outages (Days) | 24.24 | 18.37 | 12.96 | 21.97 | 15.29
16.2 | Forced Outages (Days) | 2.92 | 7.21 | 2.26 | 1.86 | 1.06
17 | Cost of spares consumed in Rs.Lakh | 1837.45 | 857.34 | 1700.72 | 1980.48 | 2054.58
18 | Average stock of spares in Rs.Lakh | 7668.32 | 7757.10 | 8226.08 | 7327.92 | 6906.58
19 | No. of employees deployed in O & M
19.1 | Executives | 226 | 221 | 217 | 218 | 234
19.2 | Non Executives | 394 | 402 | 418 | 402 | 402

## Dadri Gas 2
Performa for furnishing Actual Annual Performance / Operational data for the Gas / Liquid Fuel based thermal generating stations for the 5 year period from 2002-03 to 2006-07
1 | Name of the Company | NTPC Ltd.
2 | Name of the Station | Dadri Gas Power Sation
3 | Installed Capacity(MW) and Configuration | 829.78 MW
4 | Make of Turbine | Siemens V94.2 (130.19 MW)
5 | Rated steam parameters | BHEL (151.54 MW) - 528.6C
6 | Average stie ambient conditions | 27 DEG.C
7 | Any other Site specific feature
8 | Fuels
8.1 | Main/Primary Fuel | NATURAL GAS
8.1.1 | Annual Allocation / Requirement(MMSCM) | 1095 / 1533
8.1.2 | Sources of supply | GAIL
8.1.3 | Distance of the station from the sources of supply | 1700 KM
8.1.4 | Mode of Transport | GAIL HBJ PIPELINE
8.1.5 | Maximum Station capability to stock main fuel | NIL
8.2 | Alternative Fuel (HSD)
8.2.1 | Annual Allocation / Requirement(KL)# | 17000 KL Approx.
8.2.2 | Sources of supply | IOCL, BPCL, HPCL
8.2.3 | Distance of the station from the sources of supply | 125 (Mathura), 1400 (Mumbai), 2000 (Numali Garh
8.2.4 | Mode of Transport | BY RAIL BTPN Rake
8.2.5 | Maximum Station capability to stock secondary fuel | 17000 KL

## Dadri Gas 3
DADRI GAS
| Period | 2002-03 | 2003-04 | 2004-05 | 2005-06 | 2006-07
9 | Cost of spares
9.1 | Cost of spares capitalized in the books (Rs. Lakh) | 832.77 | 43.24
9.2 | Cost of spares included in capital cost for the purpose of tariff (Rs. Lakh) | 0.0 | 0.0
10 | Generation(MU)
10.1 | Actual Gross Generation at generator terminal
10.1.1 | Total | 5210.97 | 5060.26 | 5456.65 | 5394.14 | 5595.88
10.1.2 | On Gas
10.1.3 | On naphtha or any other liquid fuel (HSD)
10.2 | Actual Net Generation Ex-bus | 5069.18 | 4930.27 | 5319.02 | 5268.99 | 5472.76
10.3 | Scheduled Generation Ex-bus | 4954.71 | 4767.63 | 5298.21 | 5229.77 | 5420.46
11 | Average Declared Capacity (DC) (MW) | 666.40 | 705.87 | 717.39 | 724.31 | 685.61
12 | Actual Auxiliary Energy Consumption including colony consumption(MU) | 141.79 | 130.00 | 137.63 | 125.14 | 123.12
13 | Actual Energy supplied to colony from the station (MU)
14 | Main / Primary Fuel | Natural Gas
14.1 | Consmption (MMSCM) | 953.54 | 898.19 | 974.41 | 895.62 | 1004.95
14.2 | Weighted Average Gross Calorific value (As fired) (kCal/SCM) | 9101.38 | 9056.05 | 9173.42 | 9226.95 | 9273.94
14.3 | Weighted Average Price (Rs per 1000 SMC) | 3989 | 3975 | 3986 | 4613 | 6866
14.4 | Actual Average stock maintained (MT) | NIL
15 | Alternate Fuel | HSD
15.1 | Consumption (KL) | 173277.00 | 218593.58 | 207647.51 | 260001.70 | 174107.36
15.2 | Weighted Average Gross Calorific value (As fired) (kCal/L) | 9155.52 | 9029.92 | 9026.74 | 9028.85 | 9050.16
15.3 | Weighted Average Price (Rs. Per MT or KL) | 16992.6 | 18776.93 | 22887.54 | 27256.53 | 29522.1
15.4 | Actual Average stock maintained (MT or KL) | 13616.00 | 9580.16 | 17109.89 | 12252.52 | 12697.19
16 | Weighted Average duration of outages
16.1 | Scheduled Outages (Days) | 11.64 | 29.51 | 17.51 | 11.92 | 17.77
16.2 | Forced Outages (Days) | 15.48 | 1.18 | 1.07 | 4.36 | 0.26
17 | Cost of spares consumed in Rs.Lakh | 496 | 3738.37 | 954.2 | 4289.94 | 4102.33 | .
18 | Average stock of spares in Rs.Lakh | 1165.46 | 931.16 | 854.37 | 1874.93 | 2734.97
19 | No. of employees deployed in O & M
19.1 | Executives | 54 | 51 | 51 | 48 | 49
19.2 | Non Executives | 69 | 70 | 67 | 66 | 67

## FBD1
Performa for furnishing Actual Annual Performance / Operational data for the Gas / Liquid Fuel based thermal generating stations for the 5 year period from 2002-03 to 2006-07
1 | Name of the Company | NTPC Ltd.
2 | Name of the Station | Faridabad Gas Power Sation
3 | Installed Capacity(MW) and Configuration | ST=156.06, GT#1=137.758, GT#2=137.758, TOTAL = 431.586 MW
4 | Make of Turbine | Siemens V94.2 - 2 Nos. Identical
5 | Rated steam parameters | 78 KG/CM2, 528 DEG
6 | Average stie ambient conditions | 27DegC, 1.013 bar, 60% RH
7 | Any other Site specific feature
8 | Fuels
8.1 | Main/Primary Fuel | Natural Gas / RLNG
8.1.1 | Annual Allocation / Requirement(MCMD) | 570.637 | 559.3 | 604.62 | 551.45 | 555.68
|  | 589.261 | 561.783 | 605.042 | 551.853 | 561.333
8.1.2 | Sources of supply | Through HBJ Pipeline from GAIL India Ltd.
8.1.3 | Distance of the station from the sources of supply | 13 KM from Tap off point
8.1.4 | Mode of Transport | Pipeline
8.1.5 | Maximum Station capability to stock main fuel | N.A.
8.2 | Alternative Fuel (HSD) | Naptha / HSD
8.2.1 | Annual Allocation / Requirement(KL) | N=4104 | N=31834 | N=51039 | N=61934 | N=28192
|  | H=2202 | H=4496 | H=7056 | H=13125 | H=6018
|  | N=54347 | N=187458 | N=141316 | N=166875 | N=110736
|  | H=29264 | H=25562 | H=19270 | H=34189 | H=24307
8.2.2 | Sources of supply | IOCL PANIPAT
8.2.3 | Distance of the station from the sources of supply | 180 KM
8.2.4 | Mode of Transport | NAPTHA : RAIL TANKERS + PIPELINE, HSD : BY ROAD TANKERS
8.2.5 | Maximum Station capability to stock secondary fuel | NAPHTHA = 16000 KL, HSD = 500 KL

## FBD2
FARIDABAD
| Period | 2002-03 | 2003-04 | 2004-05 | 2005-06 | 2006-07
9 | Cost of spares
9.1 | Cost of spares capitalized in the books (Rs. Lakh) | 1512.23 | 488.65 | 250.46 | 111.93
9.2 | Cost of spares included in capital cost for the purpose of tariff (Rs. Lakh) | 1512.23 | 488.65
10 | Generation(MU)
10.1 | Actual Gross Generation at generator terminal
10.1.1 | Total | 2702.260 | 2788.508 | 3161.732 | 2952.795 | 2830.802
10.1.2 | On Gas
10.1.3 | On naphtha or any other liquid fuel (HSD)
10.2 | Actual Net Generation Ex-bus | 2645.352 | 2727.422 | 3099.495 | 2884.629 | 2766.567
10.3 | Scheduled Generation Ex-bus | 2673.442 | 2723.333 | 3121.851 | 2829.934 | 2720.880
11 | Average Declared Capacity (DC) (MU) / (MW) | 2906.380 | 403.748 | 410.308 | 399.389 | 372.372
12 | Actual Auxiliary Energy Consumption including colony consumption(MU) | 56.913 | 61.086 | 62.236 | 68.165 | 64.234
13 | Actual Energy supplied to colony from the station (MU)
14 | Main / Primary Fuel | NG/RLNG
14.1 | Consmption (MMSCM) | 570.355 | 559.304 | 604.62 | 551.451 | 555.686
14.2 | Weighted Average Gross Calorific value (As fired) (kCal/SMC) | 9108.929 | 9065.142 | 9134.783 | 9207.894 | 9288.830
14.3 | Weighted Average Price (Rs per 1000 SMC) | 3880 | 3860 | 3890 | 4540 | 6000
14.4 | Actual Average stock maintained (MT) | not applicable
15 | Alternate Fuel | Naphtha / HSD
15.1 | Consumption (KL) Naptha | 4101.637 | 31834.099 | 51039.579 | 61934.063 | 28192.505
15.2 | Weighted Average Gross Calorific value (As fired) (kCal/L) Naptha | 7857.089 | 7968.625 | 7924.337 | 7882.602 | 8070.040
15.3 | Weighted Average Price (Rs. Per MT or KL ) Naphtha | 16794.03 | 19498.16 | 21335.08 | 32406.59 | 35996.46
15.4 | Actual Average stock maintained (MT or KL)-- Naphtha | 3138 | 3263 | 4996 | 4165 | 5016
15.5 | Consulmption (KL) # HSD | 2202.439 | 4496.583 | 7056.208 | 13125.514 | 6018.200
15.6 | Weighted Average Gross Calorific value (As fired) (kCal/Kg or Litre) HSD | 9020.328 | 9020.328 | 9131.871 | 9094.000 | 9102.740
15.7 | Weighted Average Price (Rs.per KL) HSD | 18764.93 | 20702.58 | 23980.34 | 29569.01 | 31565.39
15.8 | Actual Average stock HSD maintained (KL) | 1780 | 803 | 291 | 324 | 385
16 | Weighted Average duration of outages
16.1 | Scheduled Outages (Days) | 42.45 | 12.81 | 9.96 | 7.04 | 23.76
16.2 | Forced Outages (Days) | 3.98 | 1.39 | 0.84 | 5.4 | 0.58
17 | Cost of spares consumed in Rs.Lakh | 1062.03 | 899.21 | 223.83 | 300.78 | 2621.82
18 | Average stock of spares in Rs.Lakh | 1407.2 | 1122.58 | 1316.84 | 1373.27 | 1309.4
19 | No. of employees deployed in O & M
19.1 | Executives | 113 | 108 | 102 | 98 | 95
19.2 | Non Executives | 55 | 55 | 55 | 56 | 55

## Anta2
1 | Name of the Company | NTPC Ltd.
2 | Name of the Station | Anta Gas Power Sation
3 | Installed Capacity(MW) and Configuration | Installed Capacity : 419 MW
Configuration : 3*88.71 + 1*53.28
4 | Make of Turbine | ABB Make 13 D2 type Gas Turbine
5 | Rated steam parameters | HP : Steam : Pressure - 62.7 bar, Temp - 485 degC, Flow:163 T/h: LP Steam: Pressure - 5.5 Bar Temp- 207 degC, Flow : 39.1 T/h
6 | Average stie ambient conditions | 27DegC, 60% RH
7 | Any other Site specific feature
8 | Fuels
8.1 | Main/Primary Fuel | Natural gas
8.1.1 | Annual Allocation/Requirement | 365 x 1.75 (MMSCM) (Linkage quantity) 365 x 2.1 (MMSCM) Requirement
8.1.2 | Sources of supply | Mumbai OFF Shore supplied by GAIL through HBJ pipeline
8.1.3 | Distance of the station from the sources of supply | 150 Kms. (approx.) from Vijaypur
8.1.4 | Mode of Transport | Pipeline
8.1.5 | Maximum Station capability to stock main fuel | NIL
8.2 | Alternative Fuel | Naphtha
8.2.1 | Annual Allocation/Requirement | Depending upon schedule
8.2.2 | Sources of supply | HPCL, BPCL, IOCL, GAIL
8.2.3 | Distance of the station from the sources of supply | GAIL (Vijaypur) : 150KM, BPCL (Mumbai) : 1000 KM, IOCL (Koyali) 700 KM, HPCL (Mumbai) 1000 KM
8.2.4 | Mode of Transport | Road Tankers
8.2.5 | Maximum Station capability to stock main fuel | Two nos. of Naphatha storage tank each having max. storage capacity of 1500 KL

## Anta3
ANTA
| Period | 2002-03 | 2003-04 | 2004-05 | 2005-06 | 2006-07
9 | Cost of spares
9.1 | Cost of spares capitalized in the books (Rs. Lakh) | 470.82 | 673.75
9.2 | Cost of spares included in capital cost for the purpose of tariff (Rs. Lakh) | 0.0 | 0.0
10 | Generation(MU)
10.1 | Actual Gross Generation at generator terminal
10.1.1 | Total | 2758.254 | 2772.455 | 2785.295 | 2809.112 | 2941.165
10.1.2 | On Gas | 2541.447 | 2348.371 | 2420.433 | 2360.20 | 2708.888
10.1.3 | On naphtha or any other liquid fuel | 216.807 | 424.084 | 364.362 | 448.912 | 232.277
10.1.2 | On Gas
10.1.3 | On naphtha or any other liquid fuel (HSD)
10.2 | Actual Net Generation Ex-bus | 2679.102 | 2701.504 | 2710.171 | 2738.388 | 2884.90
10.3 | Scheduled Generation Ex-bus | 880.6724* | 2564.968 | 2075.818 | 2713.724 | 2862.124
11 | Average Declared Capacity (DC) (MW) | 358.2135 | 352.7169 | 350.8865 | 371.5369 | 356.5029
12 | Actual Auxiliary Energy Consumption including colony consumption(MU) | 79.152 | 70.951 | 76.124 | 70.7232 | 62.6036
13 | Actual Energy supplied to colony from the station (MU)
14 | Main / Primary Fuel
14.1 | Consmption (MSMC) | 567.0296 | 541.1934 | 551.7801 | 515.325 | 563.1051
14.2 | Weighted Average Gross Calorific value (As fired) (kCal/Kg or L) -- KCAL/SCM | 9027.71 | 9073.43 | 9048.70 | 9505.98 | 9767.47
14.3 | Weighted Average Price (Rs / (1000 SCM) | 3857.51 | 3920.85 | 3863.88 | 4538.33 | 6297.86
14.4 | Actual Average stock maintained(MT or KL)
15 | Alternate Fuel
15.1 | Consumption (KL) | 54667 | 107905 | 91639 | 111215 | 58713
15.2 | Weighted Average Gross Calorific value (As fired) (kCal/L) | 8118.58 | 8066.7 | 8055.55 | 8170.71 | 8090.55
15.3 | Weighted Average Price (Rs. Per MT or KL ) | 12196.88 | 12931.5 | 16143.06 | 24230.04 | 26490.47
15.4 | Actual Average stock maintained (MT or KL) | 1661.555 | 1714.606 | 1948.337 | 2103.380 | 2026.595
16 | Weighted Average duration of outages
16.1 | Scheduled Outages (Days) | 21.63 | 22.81 | 16.57 | 12.65 | 13.97
16.2 | Forced Outages (Days) | 11.69 | 5.81 | 5.24 | 2.75 | 8.47
17 | Cost of spares consumed in Rs.Lakh | 1781.8 | 1218.22 | 1981.86 | 944.24 | 2502.49
18 | Average stock of spares in Rs.Lakh | 3397.075 | 3250.22 | 2853.13 | 2905.22 | 2935.74
19 | No. of employees deployed in O & M
19.1 | Executives | 49 | 60 | 52 | 42 | 47
19.2 | Non Executives | 77 | 78 | 79 | 82 | 80
* THIS IS AFTER ABT IMPLEMENTATION

## Auraiya1
1 | Name of the Company | NTPC Ltd.
2 | Name of the Station | Auraiya Gas Power Sation
3 | Installed Capacity(MW) and Configuration | Installed Capacity : 663.36 MW
4 Gas Turbines of 111.19 MW each & 2 Steam Turbines of 109.3 MW each
4 | Make of Turbine | MHI, Japan
5 | Rated steam parameters | 60.3 KG/Sq.cm. & 493deg C for HP Steam
6.0 KG/Sq.cm. & 158.1 deg C for LP Steam
6 | Average stie ambient conditions | Relative Humidity = 60%, Ambient Temp.=27 DegC, Ambient Pressure = 747 mmHg
7 | Any other Site specific feature | Nil
8 | Fuels
8.1 | Main/Primary Fuel | Natural gas
8.1.1 | Annual Allocation/Requirement | 2.49 MSCMD / 3.2 MSCMD
8.1.2 | Sources of supply | HBJ Pipeline (GAIL)
8.1.3 | Distance of the station from the sources of supply | 3 KM
8.1.4 | Mode of Transport | Pipeline
8.1.5 | Maximum Station capability to stock main fuel | NIL
8.2 | Alternative Fuel | Naphtha
8.2.1 | Annual Allocation/Requirement | Nil / Requirement depends upon gas allocation
8.2.2 | Sources of supply | IOCL (Mathura), BPCL (Mathura) & GAIL
8.2.3 | Distance of the station from the sources of supply | App. 250 KM from Mathura & 8 KM from GAIL Pata Plant
8.2.4 | Mode of Transport | Road Tankers
8.2.5 | Maximum Station capability to stock secondary fuel | 3000 KL (2440 Kl. Usable capability)

## Auraiya 2
Auraiya
| Period | 2002-03 | 2003-04 | 2004-05 | 2005-06 | 2006-07
9 | Cost of spares
9.1 | Cost of spares capitalized in the books (Rs. Lakh) | 2969.68 | 2309.26
9.2 | Cost of spares included in capital cost for the purpose of tariff (Rs. Lakh) | 0 | 0
10 | Generation(MU)
10.1 | Actual Gross Generation at generator terminal
10.1.1 | Total | 4268.205 | 4248.918 | 4118.465 | 4281.509 | 4613.526
10.1.2 | On Gas
10.1.3 | On naphtha
10.2 | Actual Net Generation Ex-bus | 4187.446 | 4167.859 | 4043.980 | 4204.496 | 4530.396
10.3 | Scheduled Generation Ex-bus | 4179.122 | 4091.157 | 4061.518 | 4209.057 | 4522.569
11 | Average Declared Capacity (DC) (MW) | 557.1 | 573.9 | 527.2 | 582.5 | 577.7
12 | Actual Auxiliary Energy Consumption including colony consumption(MU) | 80.759 | 81.059 | 74.485 | 77.013 | 83.130
13 | Actual Energy supplied to colony from the station (MU)
14 | Main / Primary Fuel
14.1 | Consmption (MSCM) | 813.939 | 762.810 | 772.646 | 760.145 | 915.771
14.2 | Weighted Average Gross Calorific value (As fired) (kCal/SMC) | 9317 | 9350 | 9289 | 9213.4 | 9143.0
14.3 | Weighted Average Price (Rs per 1000 SMC) | 4079.70 | 4104.39 | 4039.50 | 4630.11 | 7160.41
14.4 | Actual Average stock maintained (MT) | N.A.
15 | Alternate Fuel
15.1 | Consumption (KL) | 111496.0 | 157146.7 | 122136.0 | 171734.6 | 103170.7
15.2 | Weighted Average Gross Calorific value (As fired) (kCal/L) | 11299.0 | 11294.0 | 11326.2 | 11307.2 | 11318.4
15.3 | Weighted Average Price (Rs. Per MT) | 14952.657 | 17098.75 | 21815.03 | 32094.0 | 35549.0
15.4 | Actual Average stock maintained (MT) | 1462.0 | 1114.5 | 2089.1 | 1704.4 | 2084.1
16 | Weighted Average duration of outages
16.1 | Scheduled Outages (Days) | 18.1 | 18.2 | 13.8 | 16.7 | 15.1
16.2 | Forced Outages (Days) | 20.2 | 7.1 | 31.6 | 9.0 | 9.2
17 | Cost of spares consumed in Rs.Lakh | 2399.22 | 2661.21 | 1596.34 | 1522.93 | 1465.08
18 | Average stock of spares in Rs.Lakh | 2871 | 2731 | 2551 | 2467 | 2433
19 | No. of employees deployed in O & M
19.1 | Executives | 61 | 67 | 62 | 61 | 55
19.2 | Non Executives | 94 | 94 | 92 | 92 | 92

## Rihand2
Actual anuual performance/operational data for the coal based thermal generating satations
for the 5-year period from 2002-03 to 2006-07.
1 | Name of the Company | NTPC LTD
2 | Name of the Station | Rihand Super Thermal Power Sation,
3 | Installed Capacity(MW) and Configuration | STG-1 500 X 2 STG - II 500 X 2 STATION 2000 MW
4 | Rated Steam Parameters(Type of Steam turbine and Boiler) | STG - I Temp. 538°C Press 169.79 Kg/cm2(abs)
Turbine type - Single flow HP cylinder
Double flow IP cylinder
Two Double flow LP cylinder
Boiler type - Balance draught, signle cell, Radiant surface, controlled circulation Tangential fired boiler
STG - II Temp. 537°C Press 169.98 Kg/cm2(abs)
Turbine type - Single flow HP cylinder
Double flow IP cylinder
Double flow LP cylinder Boiler type - Balance draught ,controlled circulation, , tilting Tangential fired Boiler
5 | Type of BFP | STG - I Motor driven STG - II steam driven
6 | Circulating water system | STG-I open cycle and STG-II closed cycle
7 | Any other Site specific feature
8 | Fuels
8.1 | Main Fuel | Coal
8.1.1 | Annual Allocation/Requirement | 102.47 lac MT
8.1.2 | Sources of supply | Amlori, Dudhichua, Nigahi, Jayant, MCL, IB valley, CCL, Gurvi, ECL
8.1.3 | Distance of the station from the sources of supply | Amlori(40km), Dudhichua(53KM), Nigahi(53km), Jayant(53km), MCL(1168KM), IB valley(876KM), CCL(429KM), Gurvi(96KM), ECL(709KM)
8.1.4 | Mode of Transport | Rails/MGR
8.1.5 | Maximum Station capability to stock main fuel | 520,000MT
8.2 | Secondary Fuel | HFO/LDO
8.2.1 | Annual Allocation/Requirement | 3000KL
8.2.2 | Sources of supply | IOCL
8.2.3 | Distance of the station from the sources of supply | HFO from Haldia, LDO from Kanpur
8.2.4 | Mode of Transport | Rails & Roads
8.2.5 | Maximum Station capability to stock main fuel | HFO : 11310 KL x 2, LDO : 45 KL X 2, LDO : 250 X 1 TOTAL 22960 kl

## Rihand3
Rihand
| Period | 2002-03 | 2003-04 | 2004-05 | 2005-06 | 2006-07
9 | Cost of spares
9.1 | Cost of spares capitalized in the books (Rs. Lakh) | 355.85 | 55.21 | 39 | 1982.09
9.2 | Cost of spares included in capital cost for the purpose of tariff (Rs. Lakh) |  |  |  | 1930
10 | Generation(MU)
10.1 | Actual Gross Generation at generator terminal | 7750.446 | 7956.263 | 7988.110 | 9805.008 | 16100.321
10.2 | Actual Net Generation Ex-bus | 7127.698 | 7347.4 | 7350.947 | 9089.508 | 15055.08
10.3 | Scheduled Generation Ex-bus (MU) | 2571.77* | 7293.18 | 7230.84 | 8936.59 | 14915.35
11 | Average Declared Capacity (DC) (MW) | 902.62 | 837.31 | 828.5 | 1181.4 | 1712.26
12 | Actual Auxiliary Energy Consumption including colony consumption(MU) | 622.748 | 608.863 | 637.163 | 715.500 | 1045.240
13 | Actual Energy supplied to colony from the station (MU)
14 | Main Fuel
14.1 | Consmption (x1000 MT) | 4790.081 | 4761.92 | 4747.997 | 6182.416 | 10246.908
14.2 | Weighted Average Gross Calorific value (As fired) (kCal/Kg OR Litre)) | 3867 | 3981 | 3994 | 3775(StageI) 3667(stageII) | 3715(StageI) 3691(stageII)
14.3 | Weighted Average Price (Rs/MT) | 912.34 | 1005.51 | 1099.79 | 1147.33 | 1245
14.4 | Actual Average stock maintained (MT)** | 161845 | 154421 | 97499 | 270167 | 299096
14.5 | Actual Transit & Handling Losses for coal/Lignite (%) | 0.061 | 0.167 | 0.082 | 0.046 | 0.178
15 | Secondary Fuel Oil
15.1 | Consumption (MT/KL) | 1703.95 | 1759.5 | 1364 | 2438.324 | 2730.471
15.2 | Weighted Average Gross Calorific value (As fired) (kCal/Kg or Litre) | 9650 | 9650 | 9650 | 9650 | 9650
15.3 | Weighted Average Price (Rs. Per MT or KL) | 10046.68 | 9392.42 | 15334.41 | 19871.65 (stage I) 20954.24 (Stage II) | 23443.41 ( Stage I ) 23486.80 ( Stage II )
15.4 | Actual Average stock maintained (MT or KL) | 4093.3 | 2551.0 | 1965.5 | 2796.4 | 2582.1
16 | Weighted Average duration of outages
16.1 | Scheduled Outages (Days) | 25.26 | 25.22 | 22.7 | 14.82 | 15.77
16.2 | Forced Outages (Days) | 3.5 | 2.78 | 5.51 | 37.23 | 14.53
17 | Cost of spares consumed in Rs.Lakh | 2870.91 | 1651.15 | 2671.14 | 3325.78 | 3390.37
18 | Average stock of spares in Rs.Lakh | 7333.93 | 6499.96 | 6472.03 | 8571.63 | 11564.26
19 | Number of employees deployed in O & M
19.1 | Executives | 198 | 201 | 230 | 279 | 294
19.2 | Non-Executives | 598 | 651 | 678 | 726 | 741
* AFTER IMPLEMENTTION OF ABT

## Unchahar 2
Actual anuual performance/operational data for the coal based thermal generating satations
for the 5-year period from 2002-03 to 2006-07.
1 | Name of the Company | NTPC LTD
2 | Name of the Station | FG UNCHAHAR Thermal Power Sation
3 | Installed Capacity(MW) and Configuration | Installed Capacity : 1050 MW Configuration : 5 X 210 MW
4 | Rated Steam Parameters(Type of Steam turbine and Boiler) | Unit 1 & 2 - Pressure : 150 KscA, Temp. 535°C Unit 3,4 & 5 - Pressure : 150 KscA, Temp : 537°C Turbine - Three cylinder, Re-heat condensing Turbine. Boiler - Natural circulation, radiant, re-heat, outdoor, cool fired, tangential burner
5 | Type of BFP | Electric Driven
6 | Circulating water system | Unit 1 & 2 - Both close & open cycle. Unit 3,4 & 5 - Close cycle.
7 | Any other Site specific feature | Coal supplied by BCCL, CCL & ECL (Approx. 35 coal mines)
8 | Fuels
8.1 | Main Fuel | Coal
8.1.1 | Annual Allocation/Requirement | Allocation : 57.3 lacs MT (Average during last years) Requirement : 66 lacs MT/year (for full generation)
8.1.2 | Sources of supply | Mines from BCCL/CCL/ECL
8.1.3 | Distance of the station from the sources of supply | 650Kms. (approx.)
8.1.4 | Mode of Transport | Rails
8.1.5 | Maximum Station capability to stock main fuel | 5.50 Lacs MT (one month comsumption)
8.2 | Secondary Fuel | HFO/LDO
8.2.1 | Annual Allocation/Requirement | Requirement : 18396 KL
8.2.2 | Sources of supply | COFD Tank located at station, operated by IOC depot, Kanpur (UP)
8.2.3 | Distance of the station from the sources of supply | Approx. 150 KM
8.2.4 | Mode of Transport | Rails
8.2.5 | Maximum Station capability to stock secondary fuel | HFO : 2 x 4000 KL Tank
LDO : 1 x 4000 KL Tank
LDO : 1 x 150 KL Tank

## Unchahar 3
UNCHAHAR
| Period | 2002-03 | 2003-04 | 2004-05 | 2005-06 | 2006-07
9 | Cost of spares
9.1 | Cost of spares capitalized in the books (Rs. Lakh) | 146.5 | 733.63
9.2 | Cost of spares included in capital cost for the purpose of tariff (Rs. Lakh) | 86.2 | 687.53
10 | Generation(MU)
10.1 | Actual Gross Generation at generator terminal | 6148.8330 | 6450.9290 | 6781.0900 | 7041.2050 | 7467.2270
10.2 | Actual Net Generation Ex-bus | 5610.2425 | 5874.9597 | 6199.3938 | 6451.5851 | 6856.2778
10.3 | Scheduled Generation Ex-bus | 5232.199* | 5862.112 | 6106.934 | 6359.058 | 6766.459
11 | Average Declared Capacity (DC) (MW) | 689.856 | 680.716 | 701.457 | 731.155 | 782.393
12 | Actual Auxiliary Energy Consumption including colony consumption(MU) | 538.591 | 576.141 | 588.393 | 597.204 | 622.503
13 | Actual Energy supplied to colony from the station (MU)
14 | Main Fuel | Coal
14.1 | Consmption (MT) | 4156133 | 4424377 | 4590091 | 4734603 | 4969134
14.2 | Weighted Average Gross Calorific value (As fired) (kCal/Kg) | 3628 | 3576 | 3614 | 3609 | 3618
14.3 | Weighted Average Price (Rs/MT) | 1344.83 | 1337.46 | 1436.63 | 1497.37 | 1651.24
14.4 | Actual Average stock maintained (MT) | 357750 | 134750 | 173833 | 289500 | 206916
14.5 | Actual Transit & Handling Losses for coal/Lignite (%) | 0.654 | 0.602 | 0.598 | 0.602 | 0.596
15 | Secondary Fuel Oil | HFO / LDO
15.1 | Consumption (MT/KL) | 3907.301 | 3252.141 | 2926.957 | 2548.382 | 2049.363
15.2 | Weighted Average Gross Calorific value (As fired) (kCal/L) | 9986 | 9985 | 9986 | 9990 | 9990
15.3 | Weighted Average Price (Rs. Per MT or KL) | 10375.35 | 9830.35 | 15105.93 | 20866.98 | 24447.24
15.4 | Actual Average stock maintained (MT or KL) | Stock maintained by IOC
16 | Weighted Average duration of outages
16.1 | Scheduled Outages (Days) | 26.46 | 22.22 | 22.66 | 14.67 | 15.00
16.2 | Forced Outages (Days) | 18.81 | 14.59 | 5.62 | 4.68 | 4.37
17 | Cost of spares consumed in Rs.Lakh | 2175.08 | 2471.35 | 2221.95 | 2600.50 | 2428.12
18 | Average stock of spares in Rs.Lakh | 6561.11 | 6563.91 | 6015.24 | 6069.25 | 6832.08
19 | Number of employees deployed in O & M
19.1 | Executives | 244 | 251 | 237 | 248 | 246
19.2 | Non-Executives | 536 | 496 | 468 | 453 | 456
* AFTER IMPLEMENTTION OF ABT

## singrauli2
Actual anuual performance/operational data for the coal based thermal generating satations
for the 5-year period from 2002-03 to 2006-07.
1 | Name of the Company | NTPC Ltd.
2 | Name of the Station | Singrauli Super Thermal Power Sation,
3 | Installed Capacity(MW) and Configuration | 5*200+2*500=2000MW
4 | Rated Steam Parameters(Type of Steam turbine and Boiler) | Turbine 200 MW - 130 Ksc, 530°C Nozzle Governing Turbine 500 MW - 170 Ksc, 537°C, Throttle Governing Boiler 200 MW Tangentially Fired Balance Draft, Natural Circulation, Dry Bottom. Boiler 500 MW Tangentially Fired, Balance Draft, Forced Circulation, Dry Bottom
5 | Type of BFP | 200 MW - Electrical Driven, 500 MW - Electrical & Steam driven both.
6 | Circulating water system | Open Cycle
7 | Any other Site specific feature
8 | Fuels
8.1 | Main Fuel | Coal
8.1.1 | Annual Allocation/Requirement (MT) | 2002.03 2003-04 2004-05 2005-06 2006-07 9411000 9411000 9411000 9546000 10215000
8.1.2 | Sources of supply | NCL Jayanti (Basket Mine Dudhi Chua)
8.1.3 | Distance of the station from the sources of supply | 17.5Kms. (approx.)
8.1.4 | Mode of Transport | MGR
8.1.5 | Maximum Station capability to stock main fuel | 650000MT
8.2 | Secondary Fuel | HFO
8.2.1 | Annual Allocation/Requirement | 5000 kl
8.2.2 | Sources of supply | IOC
8.2.3 | Distance of the station from the sources of supply | -
8.2.4 | Mode of Transport | Rails
8.2.5 | Maximum Station capability to stock secondary fuel | 4*2000KL+2*4000KL+2*1000KL

## singrauli 3
SINGRAULI
| Period | 2002-03 | 2003-04 | 2004-05 | 2005-06 | 2006-07
9 | Cost of spares
9.1 | Cost of spares capitalized in the books (Rs. Lakh) | 1529.02 | 289.1 | 296.59 | 176.45
9.2 | Cost of spares included in capital cost for the purpose of tariff (Rs. Lakh) | 0.0 | 0.0
10 | Generation(MU) | - | - | - | - | -
10.1 | Actual Gross Generation at generator terminal | 16164.310 | 15641.52 | 15803.293 | 15502.75 | 14687.14
10.2 | Actual Net Generation Ex-bus | 15054.858 | 14559.262 | 14703.982 | 14400.867 | 13623.888
10.3 | Scheduled Generation Ex-bus |  | 14514.395 | 14520.438 | 14256.595 | 13499.740
11 | Average Declared Capacity (DC) (MW) |  | 1659.829 | 1662.990 | 1633.239 | 1548.569
12 | Actual Auxiliary Energy Consumption including colony consumption(MU) | 1109.452 | 1082.258 | 1099.311 | 1101.523 | 1063.252
13 | Actual Energy supplied to colony from the station (MU)
14 | Main Fuel | COAL | COAL | COAL | COAL | COAL
14.1 | Consmption (MT) | 10220887 | 9750247 | 10314328 | 10393972 | 9784606
14.2 | Weighted Average Gross Calorific value (As fired) (kCal/Kg) | 3808.3 | 3862.7 | 3692.5 | 3576.12 | 3596.98
14.3 | Weighted Average Price (Rs/MT) | 911.62 | 991.49 | 1062.76 | 1105.17 | 1096.19
14.4 | Actual Average stock maintained (MT) | 463000 | 452500 | 379500 | 332500 | 386000
14.5 | Actual Transit & Handling Losses for coal/Lignite (%) | 0.10 | 0.11 | 0.09 | 0.10 | 0.10
15 | Secondary Fuel Oil | HFO | HFO | HFO | HFO | HFO
15.1 | Consumption (MT/KL) | 2900 | 3580 | 4800 | 4868 | 6407
15.2 | Weighted Average Gross Calorific value (As fired) (kCal/L) | 9986 | 10000 | 9980 | 9986 | 9980
15.3 | Weighted Average Price (Rs. Per MT or KL) | 10287.06 | 10773.85 | 15911.28 | 20380.79 | 22416.17
15.4 | Actual Average stock maintained (MT or KL) | 4130KL | 3860KL | 2300KL | 1550KL | 2000KL
16 | Weighted Average duration of outages
16.1 | Scheduled Outages (Days) | 15.95 | 26.57 | 23.1 | 31.83 | 46.61
16.2 | Forced Outages (Days) | 4.78 | 9.0 | 7.23 | 12.92 | 13.83
17 | Cost of Spares actually consumed in Rs.Lakh | 3517.97 | 3510.34 | 5252.68 | 5170.39 | 6705.92
18 | Average stock of Spares in Rs.Lakh | 12196.59 | 11198.36 | 10967.56 | 10828.36 | 11087.51
19 | Number of employees deployed in O & M
19.1 | Executives | 362 | 329 | 314 | 319 | 318
19.2 | Non-Executives | 994 | 891 | 880 | 846 | 820

## simhadri2
Actual anuual performance/operational data for the coal based thermal generating satations
for the 5-year period from 2002-03 to 2006-07.
1 | Name of the Company | NTPC Ltd.
2 | Name of the Station | Simhadri Thermal Power Sation,
3 | Installed Capacity(MW) and Configuration | 1000 MW (2x500 MW)
4 | Rated Steam Parameters(Type of Steam turbine and Boiler) | Boiler : Controlled circulation with rifled tubing, dry bottom, radiant, reheat, balanced draft furnace. Main steam 537 Deg C & 170 Kg/cm2. Turbine 3-cylinder reheat, condensing type.
5 | Type of BFP | Steam Driven
6 | Circulating water system | Closed Cycle
7 | Any other Site specific feature | 1. Sea water for CW system & ash disposal. Single beneficiary state is Andhra Pradesh.
8 | Fuels
8.1 | Main Fuel | Coal
8.1.1 | Annual Allocation/Requirement | 50,00,000 MT
8.1.2 | Sources of supply | Mahanadi Coal Fields Ltd., Orissa
8.1.3 | Distance of the station from the sources of supply | 600 Kms. (approx.)
8.1.4 | Mode of Transport | Rails
8.1.5 | Maximum Station capability to stock main fuel | 4,50,000MT
8.2 | Secondary Fuel | LDO & HFO
8.2.1 | Annual Allocation/Requirement | LDO - 1500 KL; HFO - 2500 KL
8.2.2 | Sources of supply | IOC, Vishakhapatnam
8.2.3 | Distance of the station from the sources of supply | 50Kms. (Approx.)
8.2.4 | Mode of Transport | Road
8.2.5 | Maximum Station capability to stock secondary fuel | LDO - 1000 KL; HFO - 4000 KL

## simhadri3
SIMHADRI
| Period | 2002-03 | 2003-04 | 2004-05 | 2005-06 | 2006-07
9 | Cost of spares
9.1 | Cost of spares capitalized in the books (Rs. Lakh) | 2008.8 | 2220.45 | 982.17 | 96.09
9.2 | Cost of spares included in capital cost for the purpose of tariff (Rs. Lakh) | 2008.8 | 2220.45
10 | Generation(MU) | - | - | - | - | -
10.1 | Actual Gross Generation at generator terminal | 2464.96 | 7722.54 | 8122.68 | 7741.68 | 8068.16
10.2 | Actual Net Generation Ex-bus | 2316.88 | 7245.23 | 7663.71 | 7303.98 | 7619.87
10.3 | Scheduled Generation Ex-bus |  |  |  |  | 7562.94
11 | Average Declared Capacity (DC) (MW) |  |  |  |  | 872.59
12 | Actual Auxiliary Energy Consumption including colony consumption(MU) | 148.08 | 477.31 | 458.97 | 437.7 | 448.29
13 | Actual Energy supplied to colony from the station (MU)
14 | Main Fuel
14.1 | Consmption (MT) | 1714809 | 5245549 | 5524321 | 5067341 | 5499715
14.2 | Weighted Average Gross Calorific value (As fired) (kCal/Kg) | 3488.39 | 3529.58 | 3488.26 | 3604.89 | 3451.75
14.3 | Weighted Average Price (Rs/MT) | 1023.37 | 1004.17 | 1073.86 | 1274.77 | 1196.22
14.4 | Actual Average stock maintained (MT) | 316490 | 162508 | 95412 | 267351 | 342816
14.5 | Actual Transit & Handling Losses for coal/Lignite (%) | 0.55 | 0.57 | 0.17 | 0.54 | 0.72
15 | Secondary Fuel Oil
15.1 | Consumption (KL) | 2707 | 5107 | 1872 | 1484 | 1507
15.2 | Weighted Average Gross Calorific value (As fired) (kCal/L) | 9767.58 | 9738.1 | 9720.74 | 9704.81 | 9705.81
15.3 | Weighted Average Price (Rs. Per MT or KL) | 14310.03 | 15504.88 | 16906.14 | 25077.74 | 28087.11
15.4 | Actual Average stock maintained (MT or KL) | 4749 | 2900 | 1885 | 1049 | 996
16 | Weighted Average duration of outages
16.1 | Scheduled Outages (Days) | 15 | 13.38 | 19.22 | 16.52 | 22.77
16.2 | Forced Outages (Days) | 15.44 | 17.17 | 5.47 | 6.39 | 4.82
17 | Cost of spares consumed in Rs.Lakh | 46 | 629 | 2086 | 1212 | 1236
18 | Average stock of spares in Rs.Lakhs | 147 | 2919 | 5529 | 5398 | 5475
19 | Number of employees deployed in O & M
19.1 | Executives | 359 | 329 | 305 | 294 | 301
19.2 | Non Executives | 230 | 224 | 218 | 213 | 208

## RGCCPP2
THE 5 YEAR PERIOD FROM 2002-03 TO 2006-07
1 | Name of the Company | NTPC Ltd.
2 | Name of the Station | Rajiv Gandhi Combined Cycle Power Sation
3 | Installed Capacity(MW) and Configuration | GT 115.2 X 2 = 230.400 MW
STG 129.177 = 129.177 MW
TOTAL = 359.577 MW
4 | Make of Turbine | Gas Turbine - G.E., USA, Steam Turbine - BHEL, Hardwar
5 | Rated steam parameters | HP : Steam : Pressure - 76 ata; Temp - 518.2 degC, Flow:376.8 T/h: LP Steam: Pressure - 5.418ata, Temp- 183 degC, Flow : 431.29 T/h
6 | Average stie ambient conditions | Relative Humidity : 80%, Amb Temp: 28 deg C
7 | Any other Site specific feature | Grid Frequency is generally very low <49.3 Hz
8 | Fuels | Naptha & HSD
8.1 | Main/Primary Fuel | Naptha
8.1.1 | Annual Allocation/Requirement | As per the station schedule
8.1.2 | Sources of supply | BPCL, Kochin refinery Ltd., Cochin.
8.1.3 | Distance of the station from the sources of supply | 120 Kms. (approx.)
8.1.4 | Mode of Transport | Rails
8.1.5 | Maximum Station capability to stock main fuel | 40,000kL
8.2 | Alternative Fuel | HSD
8.2.1 | Annual Allocation/Requirement | As per the station schedule
8.2.2 | Sources of supply | BPCL, Kochin refinery Ltd., Cochin.
8.2.3 | Distance of the station from the sources of supply | 120Kms. (Approx.)
8.2.4 | Mode of Transport | Road
8.2.5 | Maximum Station capability to stock sec fuel | 365 Kl

## RGCCPP3
RGCPP
| Period | 2002-03 | 2003-04 | 2004-05 | 2005-06 | 2006-07
9 | Cost of spares
9.1 | Cost of spares capitalized in the books (Rs.Lakh) | 776.67 | 945.15
9.2 | Cost of spares included in capital cost for the purpose of tariff (Rs.Lakh) | 776.67 | 945.15
10 | Generation(MU)
10.1 | Actual Gross Generation at generator terminal
10.1.1 | Total | 2118.508 | 2117.974 | 621.737 | 358.447 | 1137.354
10.1.2 | On Gas
10.1.3 | On naphtha
10.2 | Actual Generation ex-bus | 2072.47 | 2069.009 | 596.496 | 336.086 | 1107.561
10.3 | Scheduled Generation Ex-bus |  |  | 612.411 | 350.781 | 1114.286
11 | Average Declared Capacity (DC) (MU) |  |  | 295.853 | 334.61 | 325.741
12 | Actual Auxiliary Energy Consumption including colony consumption(MU) | 45.776 | 48.74 | 25.033 | 22.147 | 29.54
13 | Actual Energy supplied to colony from the station (MU)
14 | Main/Primary Fuel | NAPTHA | NAPTHA | NAPTHA | NAPTHA | NAPTHA
14.1 | Consmption (MT) | 368978.5 | 369420.2 | 107809.5 | 62408.3 | 196261.1
14.2 | Weighted Average Gross Calorific value (As fired) (kCal/Kg) | 11341 | 11347 | 11350 | 11341 | 11338 | 10.1.2 | On Gas | 0 | 0 | 0 | 0 | 0
14.3 | Weighted Average Price (Rs/MT) | 14926.73 | 14586.4 | 19101.1 | 22063.04 | 32158.61 | 10.1.3 | On Naptha or any other liquid fuel | 2118.508 | 2117.974 | 621.737 | 358.447 | 1137.354
14.4 | Actual Average stock maintained (MT) | 15383.13 | 16451.15 | 12489.19 | 17599.3 | 7485.55
15 | Alternative Fuel | HSD | HSD | HSD | HSD | HSD
15.1 | Consumption (KL) | 393.8 | 260.35 | 249.86 | 466.9 | 455.6
15.2 | Weighted Average Gross Calorific value (As fired) (kCal/L) | 9048 | 9045 | 9060 | 9077 | 9077
15.3 | Weighted Average Price (Rs. Per MT or KL) | 16171.32 | 17424.97 | 19248.83 | 24081.33 | 28255.17
15.4 | Actual Average stock maintained (MT or KL) | 323.848 | 309.84 | 267.209 | 230.794 | 251.909
16 | Weighted Average duration of outages
16.1 | Scheduled Outages (Days) | 16.08 | 28.75 | 34.93 | 0.97 | 6.673
16.2 | Forced Outages (Days) | 4.81 | 4.89 | 0.87 | 0 | 1.735
17 | Cost of spares consumed in Rs.Lakh | 452.48 | 728.53 | 269.62 | 259.08 | 235.03
18 | Average stock of spares in Rs.Lakhs | 1616.68 | 1695.21 | 1922.97 | 2164.85 | 2225.18
19 | Number of employees deployed in O & M
19.1 | Executives | 94 | 97 | 88 | 76 | 74
19.2 | Non Executives | 76 | 77 | 72 | 72 | 84

## Gandhar 1
Actual anuual performance/operational data for the coal based thermal generating satations
for the 5-year period from 2002-03 to 2006-07.
1 | Name of the Company | NTPC Ltd.
2 | Name of the Station | Jhanor Gandhar Gas Power Station
3 | Installed Capacity(MW) and Configuration | Gas Turbine : 03 Nos x 144.3 MW each
Steam Turbine : 01 No. X 224.49 MW
Station : 657.39
4 | Make of Turbine | ABB
5 | Rated Steam Parameters(Type of Steam turbine and Boiler) | Steam Inlet Pressure 66.49 Bar, Temp. 501.8 deg C, Steam Exhaust Pressure 100 mbar
6 | Average site ambient conditions | Ambient Dry Bulb Temp. : 27.0 deg C
Ambient Air Pressure : 1010 mbar
Ambient Relative Humidity : 60%
7 | Any other Site specific feature
8 | Fuels
8.1 | Main Fuel | Natural Gas, RLNG
8.1.1 | Annual Allocation/Requirement | 3.20 Million Cubic Mr Per Day (MCMD)
8.1.2 | Sources of supply | a) Gandhar gas fields, b) HVJ Pipeline, c) GSPL Pipeline
8.1.3 | Distance of the station from the sources of supply | Gandhar Gas Field - 50 KMs approx. HVJP - 25 KMs approx,GSPL Pipeline -14 KMs.Approx.
8.1.4 | Mode of Transport | Pipeline
8.1.5 | Maximum Station capability to stock main fuel | Not Applicable
8.2 | Secondary Fuel | Not Applicable
8.2.1 | Annual Allocation/Requirement | Not Applicable
8.2.2 | Sources of supply | Not Applicable
8.2.3 | Distance of the station from the sources of supply | Not Applicable
8.2.4 | Mode of Transport | Not Applicable
8.2.5 | Maximum Station capability to stock secondary fuel | Not Applicable

## Gandhar 2
[25 empty] | Gandhar |  | 16 | APC from ex bus
| GANDHAR | [25 empty] | Weighted Average duration of outages | Scheduled Outages (Days)
| Period | 2002-03 | 2003-04 | 2004-05 | 2005-06 | 2006-07 | [20 empty] | N.A. | 8.21
9 | Cost of spares | [25 empty] | N.A. | 8.441
9.1 | Cost of spares capitalized in the books (Rs. Lakh) | 1384.93 | 819.95 | [23 empty] | N.A. | 12.25
9.2 | Cost of spares included in capital cost for the purpose of tariff (Rs. Lakh) | nil | nil | [23 empty] | N.A. | 19.948
10 | Generation(MU) | (Jul02-Mar03) | [24 empty] | N.A. | 14.798
10.1 | Actual Gross Generation at generator terminal
10.1.1 | Total | 2678.363 | 3220.204 | 4031.711 | 4477.775 | 4555.46
10.1.2 | On Gas
10.1.3 | On naphtha
10.2 | Actual Net Generation Ex-bus (MW) | 397.94 | 358.08 | 450.88 | 501.14 | 509.87 | [19 empty] | FARIDABAD
10.3 | Scheduled Generation Ex-bus (MW) | 395.17 | 357.39 | 446.03 | 498.99 | 503.41
11 | Average Declared Capacity (DC) (MW) | 407.7 | 367.59 | 454.08 | 516.11 | 524.59
12 | Actual Auxiliary Energy Consumption including colony consumption(MU) | 59.43 | 74.96 | 82.015 | 87.499 | 88.999
13 | Actual Energy supplied to colony from the station (MU)
14 | Main / Primary Fuel | Natural Gas
14.1 | Consmption (MSCM) | 546.0508 | 660.4517 | 819.1239 | 921.1112 | 940.885
14.2 | Weighted Average Gross Calorific value (As fired) (kCal/SMC) | 9487.65 | 9547.79 | 9828.09 | 9809.87 | 9808.69
14.3 | Weighted Average Price (Rs per 1000 SMC) | 4772.48 | 4886.54 | 4776.85 | 6399.28 | 8182.26
14.4 | Actual Average stock maintained (MT) | N.A. | N.A. | N.A. | N.A. | N.A.
15a | Alternate Fuel (NAPHTHA)
15.1 | Consumption (KL) | N.A. | N.A. | N.A. | N.A. | N.A.
15.2 | Weighted Average Gross Calorific value (As fired) (kCal/L) | N.A. | N.A. | N.A. | N.A. | N.A.
15.3 | Weighted Average Price (Rs. Per MT or KL) | N.A. | N.A. | N.A. | N.A. | N.A.
15.4 | Actual Average stock maintained (MT or KL) | N.A. | N.A. | N.A. | N.A. | N.A.
16 | Weighted Average duration of outages | N.A. | N.A. | N.A. | N.A. | N.A.
16.1 | Scheduled Outages (Days) | 8.21 | 8.441 | 12.25 | 19.948 | 14.798
16.2 | Forced outages (days) | 1.675 | 2.983 | 1.456 | 0.136 | 0.267
17 | Cost of spares consumed in Rs. Lakhs | 1021.02 | 428.06 | 1175.74 | 1840.8 | 1879.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18 | Average stock of spares in Rs. Lakh | 5683.68 | 4586.14 | 4522.79 | 4491.18 | 4591.08
19 | Number of employees deployed in O & M | [24 empty] | Gandhar
19.1 | Executives | 98 | 97 | 97 | 114 | 113
19.2 | Non-Executives | 100 | 99 | 100 | 94 | 91